## Input
Parameter | Value
Source Voltage (VDC) | 100
Source Internal Resistance (Ohms) | 0.01
Line Resistance (Ohms/km) | 0.02
Fault Resistance (Ohms) | 0.01
Fault Distance from Nearest Substation (km) | 1
Number of Substations | 3
Substation Spacing (km) | 5
Protection Trip Time (seconds) | 0.1
Protection Trip Current (Amps) | 4000
System Inductance (H) | 0.001
Line Inductance (H/km) | 0.0005

## Results
Result | Value
Total Fault Current (Amps) | 4000
Energy Released (Joules) | 16000
Thermal Stress (A*sqrt(s)) | 1264.9111
Protection Will Trip | Yes
Trip Time (s) | 100
Shortest Distance Fault Current (Amps) | 5000
Longest Distance Fault Current (Amps) | 1428.5714
Shortest Distance Current Rate of Change (kA/s) | 100000
Longest Distance Current Rate of Change (kA/s) | 44444.4444
Peak Current Rate of Change (kA/s) | 66.6667
Steady State Current Rate of Change (kA/s) | 0.005903

## Generator
Substation | Location (km) | Distance to Fault (km) | Fault Current (Amps) | Voltage Drop (V) | Contribution (%)
Substation 1 | 0 | 1 | 2500 | 50 | 62.5
Substation 2 | 5 | 4 | 1000 | 80 | 25
Substation 3 | 10 | 9 | 500 | 90 | 12.5

## Time Domain Data
Time (ms) | Electric Current (A) | di/dt (kA/s) | Filtered di/dt (kA/s) | Voltage (V)
0 | 0 | 0 | 0 | 0
0.1 | 6.6578 | 66.6667 | 0.062979 | 100
0.2 | 13.2978 | 66.4006 | 0.30905 | 99.6008
0.3 | 19.9202 | 66.2237 | 0.78403 | 99.3356
0.4 | 26.5249 | 66.0474 | 1.4659 | 99.071
0.5 | 33.1121 | 65.8715 | 2.3339 | 98.8072
0.6 | 39.6817 | 65.696 | 3.3681 | 98.5441
0.7 | 46.2338 | 65.5211 | 4.5499 | 98.2816
0.8 | 52.7685 | 65.3466 | 5.8617 | 98.0199
0.9 | 59.2857 | 65.1726 | 7.2866 | 97.7589
1 | 65.7856 | 64.999 | 8.8092 | 97.4985
1.1 | 72.2682 | 64.8259 | 10.4147 | 97.2389
1.2 | 78.7335 | 64.6533 | 12.0892 | 96.9799
1.3 | 85.1817 | 64.4811 | 13.82 | 96.7216
1.4 | 91.6126 | 64.3094 | 15.5951 | 96.4641
1.5 | 98.0264 | 64.1381 | 17.4033 | 96.2072
1.6 | 104.4231 | 63.9673 | 19.2344 | 95.951
1.7 | 110.8028 | 63.7969 | 21.0788 | 95.6954
1.8 | 117.1655 | 63.6271 | 22.9279 | 95.4406
1.9 | 123.5113 | 63.4576 | 24.7735 | 95.1864
2 | 129.8402 | 63.2886 | 26.6084 | 94.9329
2.1 | 136.1522 | 63.1201 | 28.4258 | 94.6801
2.2 | 142.4474 | 62.952 | 30.2199 | 94.428
2.3 | 148.7258 | 62.7843 | 31.9851 | 94.1765
2.4 | 154.9875 | 62.6171 | 33.7166 | 93.9257
2.5 | 161.2325 | 62.4504 | 35.4101 | 93.6755
2.6 | 167.4609 | 62.2841 | 37.0617 | 93.4261
2.7 | 173.6728 | 62.1182 | 38.6683 | 93.1773
2.8 | 179.868 | 61.9528 | 40.2269 | 92.9291
2.9 | 186.0468 | 61.7878 | 41.735 | 92.6816
3 | 192.2091 | 61.6232 | 43.1907 | 92.4348
3.1 | 198.355 | 61.4591 | 44.5923 | 92.1887
3.2 | 204.4846 | 61.2954 | 45.9384 | 91.9432
3.3 | 210.5978 | 61.1322 | 47.2282 | 91.6983
3.4 | 216.6947 | 60.9694 | 48.4608 | 91.4541
3.5 | 222.7755 | 60.807 | 49.6359 | 91.2105
3.6 | 228.84 | 60.6451 | 50.7532 | 90.9676
3.7 | 234.8883 | 60.4836 | 51.813 | 90.7254
3.8 | 240.9206 | 60.3225 | 52.8154 | 90.4838
3.9 | 246.9368 | 60.1619 | 53.7609 | 90.2428
4 | 252.9369 | 60.0016 | 54.6503 | 90.0025
4.1 | 258.9211 | 59.8419 | 55.4842 | 89.7628
4.2 | 264.8894 | 59.6825 | 56.2638 | 89.5237
4.3 | 270.8417 | 59.5236 | 56.9899 | 89.2853
4.4 | 276.7782 | 59.365 | 57.6639 | 89.0475
4.5 | 282.6989 | 59.2069 | 58.287 | 88.8104
4.6 | 288.6038 | 59.0493 | 58.8606 | 88.5739
4.7 | 294.493 | 58.892 | 59.3862 | 88.338
4.8 | 300.3666 | 58.7352 | 59.8652 | 88.1028
4.9 | 306.2244 | 58.5788 | 60.2992 | 87.8681
5 | 312.0667 | 58.4228 | 60.6898 | 87.6341
5.1 | 317.8934 | 58.2672 | 61.0386 | 87.4007
5.2 | 323.7046 | 58.112 | 61.3473 | 87.168
5.3 | 329.5003 | 57.9572 | 61.6175 | 86.9358
5.4 | 335.2806 | 57.8029 | 61.8509 | 86.7043
5.5 | 341.0455 | 57.649 | 62.0492 | 86.4734
5.6 | 346.7951 | 57.4954 | 62.214 | 86.2431
5.7 | 352.5293 | 57.3423 | 62.3469 | 86.0135
5.8 | 358.2483 | 57.1896 | 62.4497 | 85.7844
5.9 | 363.952 | 57.0373 | 62.5238 | 85.5559
6 | 369.6405 | 56.8854 | 62.5709 | 85.3281
6.1 | 375.3139 | 56.7339 | 62.5925 | 85.1009
6.2 | 380.9722 | 56.5828 | 62.5901 | 84.8742
6.3 | 386.6154 | 56.4321 | 62.5652 | 84.6482
6.4 | 392.2436 | 56.2818 | 62.5193 | 84.4228
6.5 | 397.8568 | 56.132 | 62.4537 | 84.1979
6.6 | 403.455 | 55.9825 | 62.3698 | 83.9737
6.7 | 409.0384 | 55.8334 | 62.2689 | 83.7501
6.8 | 414.6069 | 55.6847 | 62.1522 | 83.527
6.9 | 420.1605 | 55.5364 | 62.0211 | 83.3046
7 | 425.6993 | 55.3885 | 61.8766 | 83.0828
7.1 | 431.2234 | 55.241 | 61.7198 | 82.8615
7.2 | 436.7328 | 55.0939 | 61.5519 | 82.6408
7.3 | 442.2275 | 54.9472 | 61.3739 | 82.4207
7.4 | 447.7076 | 54.8008 | 61.1867 | 82.2012
7.5 | 453.1731 | 54.6549 | 60.9913 | 81.9823
7.6 | 458.6241 | 54.5093 | 60.7886 | 81.764
7.7 | 464.0605 | 54.3642 | 60.5794 | 81.5463
7.8 | 469.4824 | 54.2194 | 60.3645 | 81.3291
7.9 | 474.8899 | 54.075 | 60.1446 | 81.1125
8 | 480.283 | 53.931 | 59.9205 | 80.8965
8.1 | 485.6617 | 53.7874 | 59.6928 | 80.6811
8.2 | 491.0262 | 53.6441 | 59.4622 | 80.4662
8.3 | 496.3763 | 53.5013 | 59.2292 | 80.2519
8.4 | 501.7122 | 53.3588 | 58.9943 | 80.0382
8.5 | 507.0338 | 53.2167 | 58.7582 | 79.825
8.6 | 512.3413 | 53.075 | 58.5211 | 79.6124
8.7 | 517.6347 | 52.9336 | 58.2837 | 79.4004
8.8 | 522.914 | 52.7927 | 58.0462 | 79.189
8.9 | 528.1792 | 52.6521 | 57.809 | 78.9781
9 | 533.4303 | 52.5118 | 57.5726 | 78.7678
9.1 | 538.6675 | 52.372 | 57.3371 | 78.558
9.2 | 543.8908 | 52.2325 | 57.1029 | 78.3488
9.3 | 549.1001 | 52.0934 | 56.8701 | 78.1401
9.4 | 554.2956 | 51.9547 | 56.6392 | 77.932
9.5 | 559.4772 | 51.8163 | 56.4101 | 77.7245
9.6 | 564.6451 | 51.6783 | 56.1832 | 77.5175
9.7 | 569.7991 | 51.5407 | 55.9586 | 77.3111
9.8 | 574.9395 | 51.4035 | 55.7363 | 77.1052
9.9 | 580.0662 | 51.2666 | 55.5166 | 76.8998
10 | 585.1792 | 51.13 | 55.2995 | 76.695
10.1 | 590.2785 | 50.9939 | 55.0851 | 76.4908
10.2 | 595.3643 | 50.8581 | 54.8735 | 76.2871
10.3 | 600.4366 | 50.7226 | 54.6647 | 76.0839
10.4 | 605.4954 | 50.5875 | 54.4587 | 75.8813
10.5 | 610.5406 | 50.4528 | 54.2557 | 75.6792
10.6 | 615.5725 | 50.3185 | 54.0555 | 75.4777
10.7 | 620.5909 | 50.1845 | 53.8582 | 75.2767
10.8 | 625.596 | 50.0508 | 53.6638 | 75.0762
10.9 | 630.5878 | 49.9175 | 53.4723 | 74.8763
11 | 635.5662 | 49.7846 | 53.2837 | 74.6769
11.1 | 640.5314 | 49.652 | 53.0978 | 74.478
11.2 | 645.4834 | 49.5198 | 52.9148 | 74.2797
11.3 | 650.4222 | 49.3879 | 52.7345 | 74.0818
11.4 | 655.3478 | 49.2564 | 52.5568 | 73.8846
11.5 | 660.2604 | 49.1252 | 52.3818 | 73.6878
11.6 | 665.1598 | 48.9944 | 52.2094 | 73.4916
11.7 | 670.0462 | 48.8639 | 52.0395 | 73.2958
11.8 | 674.9196 | 48.7338 | 51.872 | 73.1006
11.9 | 679.78 | 48.604 | 51.7069 | 72.906
12 | 684.6274 | 48.4745 | 51.5441 | 72.7118
12.1 | 689.462 | 48.3454 | 51.3836 | 72.5182
12.2 | 694.2836 | 48.2167 | 51.2252 | 72.325
12.3 | 699.0925 | 48.0883 | 51.069 | 72.1324
12.4 | 703.8885 | 47.9602 | 50.9147 | 71.9403
12.5 | 708.6717 | 47.8325 | 50.7624 | 71.7488
12.6 | 713.4422 | 47.7051 | 50.612 | 71.5577
12.7 | 718.2 | 47.5781 | 50.4634 | 71.3671
12.8 | 722.9452 | 47.4514 | 50.3165 | 71.1771
12.9 | 727.6777 | 47.325 | 50.1713 | 70.9875
13 | 732.3976 | 47.199 | 50.0277 | 70.7985
13.1 | 737.1049 | 47.0733 | 49.8856 | 70.6099
13.2 | 741.7997 | 46.9479 | 49.7449 | 70.4219
13.3 | 746.482 | 46.8229 | 49.6057 | 70.2343
13.4 | 751.1518 | 46.6982 | 49.4677 | 70.0473
13.5 | 755.8092 | 46.5738 | 49.331 | 69.8607
13.6 | 760.4542 | 46.4498 | 49.1956 | 69.6747
13.7 | 765.0868 | 46.3261 | 49.0613 | 69.4891
13.8 | 769.707 | 46.2027 | 48.928 | 69.3041
13.9 | 774.315 | 46.0797 | 48.7958 | 69.1195
14 | 778.9107 | 45.957 | 48.6646 | 68.9354
14.1 | 783.4942 | 45.8346 | 48.5343 | 68.7519
14.2 | 788.0654 | 45.7125 | 48.4048 | 68.5688
14.3 | 792.6245 | 45.5908 | 48.2762 | 68.3862
14.4 | 797.1714 | 45.4694 | 48.1484 | 68.204
14.5 | 801.7063 | 45.3483 | 48.0214 | 68.0224
14.6 | 806.229 | 45.2275 | 47.895 | 67.8413
14.7 | 810.7397 | 45.1071 | 47.7693 | 67.6606
14.8 | 815.2384 | 44.9869 | 47.6442 | 67.4804
14.9 | 819.7251 | 44.8671 | 47.5198 | 67.3007
15 | 824.1999 | 44.7476 | 47.3958 | 67.1215
15.1 | 828.6627 | 44.6285 | 47.2725 | 66.9427
15.2 | 833.1137 | 44.5096 | 47.1496 | 66.7644
15.3 | 837.5528 | 44.3911 | 47.0271 | 66.5866
15.4 | 841.9801 | 44.2729 | 46.9052 | 66.4093
15.5 | 846.3956 | 44.155 | 46.7836 | 66.2324
15.6 | 850.7993 | 44.0374 | 46.6625 | 66.0561
15.7 | 855.1913 | 43.9201 | 46.5417 | 65.8801
15.8 | 859.5716 | 43.8031 | 46.4213 | 65.7047
15.9 | 863.9403 | 43.6865 | 46.3013 | 65.5297
16 | 868.2973 | 43.5701 | 46.1815 | 65.3552
16.1 | 872.6427 | 43.4541 | 46.0621 | 65.1812
16.2 | 876.9766 | 43.3384 | 45.943 | 65.0076
16.3 | 881.2989 | 43.223 | 45.8242 | 64.8345
16.4 | 885.6096 | 43.1079 | 45.7056 | 64.6618
16.5 | 889.9089 | 42.9931 | 45.5873 | 64.4896
16.6 | 894.1968 | 42.8786 | 45.4693 | 64.3178
16.7 | 898.4732 | 42.7644 | 45.3515 | 64.1466
16.8 | 902.7383 | 42.6505 | 45.2339 | 63.9757
16.9 | 906.992 | 42.5369 | 45.1166 | 63.8054
17 | 911.2343 | 42.4236 | 44.9995 | 63.6354
17.1 | 915.4654 | 42.3106 | 44.8827 | 63.466
17.2 | 919.6852 | 42.198 | 44.766 | 63.297
17.3 | 923.8938 | 42.0856 | 44.6496 | 63.1284
17.4 | 928.0911 | 41.9735 | 44.5333 | 62.9603
17.5 | 932.2773 | 41.8617 | 44.4173 | 62.7926
17.6 | 936.4523 | 41.7502 | 44.3015 | 62.6254
17.7 | 940.6162 | 41.6391 | 44.1859 | 62.4586
17.8 | 944.769 | 41.5282 | 44.0705 | 62.2923
17.9 | 948.9108 | 41.4176 | 43.9553 | 62.1264
18 | 953.0415 | 41.3073 | 43.8403 | 61.9609
18.1 | 957.1612 | 41.1973 | 43.7256 | 61.7959
18.2 | 961.27 | 41.0876 | 43.611 | 61.6313
18.3 | 965.3678 | 40.9781 | 43.4966 | 61.4672
18.4 | 969.4547 | 40.869 | 43.3824 | 61.3035
18.5 | 973.5307 | 40.7602 | 43.2685 | 61.1403
18.6 | 977.5959 | 40.6516 | 43.1547 | 60.9774
18.7 | 981.6502 | 40.5434 | 43.0412 | 60.815
18.8 | 985.6938 | 40.4354 | 42.9279 | 60.6531
18.9 | 989.7265 | 40.3277 | 42.8148 | 60.4916
19 | 993.7486 | 40.2203 | 42.7019 | 60.3305
19.1 | 997.7599 | 40.1132 | 42.5893 | 60.1698
19.2 | 1001.7605 | 40.0064 | 42.4768 | 60.0096
19.3 | 1005.7505 | 39.8998 | 42.3646 | 59.8497
19.4 | 1009.7299 | 39.7936 | 42.2526 | 59.6904
19.5 | 1013.6986 | 39.6876 | 42.1409 | 59.5314
19.6 | 1017.6568 | 39.5819 | 42.0293 | 59.3729
19.7 | 1021.6045 | 39.4765 | 41.918 | 59.2147
19.8 | 1025.5416 | 39.3714 | 41.807 | 59.057
19.9 | 1029.4683 | 39.2665 | 41.6962 | 58.8998
20 | 1033.3845 | 39.1619 | 41.5856 | 58.7429
20.1 | 1037.2902 | 39.0576 | 41.4753 | 58.5865
20.2 | 1041.1856 | 38.9536 | 41.3652 | 58.4304
20.3 | 1045.0706 | 38.8499 | 41.2554 | 58.2748
20.4 | 1048.9452 | 38.7464 | 41.1458 | 58.1196
20.5 | 1052.8095 | 38.6432 | 41.0364 | 57.9649
20.6 | 1056.6636 | 38.5403 | 40.9273 | 57.8105
20.7 | 1060.5073 | 38.4377 | 40.8185 | 57.6565
20.8 | 1064.3409 | 38.3353 | 40.7099 | 57.503
20.9 | 1068.1642 | 38.2332 | 40.6016 | 57.3499
21 | 1071.9773 | 38.1314 | 40.4936 | 57.1971
21.1 | 1075.7803 | 38.0299 | 40.3858 | 57.0448
21.2 | 1079.5732 | 37.9286 | 40.2783 | 56.8929
21.3 | 1083.3559 | 37.8276 | 40.171 | 56.7414
21.4 | 1087.1286 | 37.7268 | 40.064 | 56.5903
21.5 | 1090.8913 | 37.6264 | 39.9573 | 56.4396
21.6 | 1094.6439 | 37.5262 | 39.8508 | 56.2893
21.7 | 1098.3865 | 37.4262 | 39.7446 | 56.1394
21.8 | 1102.1192 | 37.3266 | 39.6387 | 55.9899
21.9 | 1105.8419 | 37.2272 | 39.533 | 55.8407
22 | 1109.5547 | 37.128 | 39.4276 | 55.692
22.1 | 1113.2576 | 37.0291 | 39.3225 | 55.5437
22.2 | 1116.9507 | 36.9305 | 39.2177 | 55.3958
22.3 | 1120.6339 | 36.8322 | 39.1131 | 55.2483
22.4 | 1124.3073 | 36.7341 | 39.0088 | 55.1011
22.5 | 1127.9709 | 36.6363 | 38.9048 | 54.9544
22.6 | 1131.6248 | 36.5387 | 38.801 | 54.8081
22.7 | 1135.2689 | 36.4414 | 38.6975 | 54.6621
22.8 | 1138.9034 | 36.3443 | 38.5943 | 54.5165
22.9 | 1142.5281 | 36.2476 | 38.4914 | 54.3713
23 | 1146.1432 | 36.151 | 38.3887 | 54.2265
23.1 | 1149.7487 | 36.0548 | 38.2863 | 54.0821
23.2 | 1153.3446 | 35.9587 | 38.1842 | 53.9381
23.3 | 1156.9309 | 35.863 | 38.0824 | 53.7945
23.4 | 1160.5076 | 35.7675 | 37.9808 | 53.6512
23.5 | 1164.0748 | 35.6722 | 37.8795 | 53.5083
23.6 | 1167.6325 | 35.5772 | 37.7785 | 53.3658
23.7 | 1171.1808 | 35.4825 | 37.6777 | 53.2237
23.8 | 1174.7196 | 35.388 | 37.5772 | 53.082
23.9 | 1178.249 | 35.2937 | 37.477 | 52.9406
24 | 1181.7689 | 35.1997 | 37.3771 | 52.7996
24.1 | 1185.2795 | 35.106 | 37.2774 | 52.659
24.2 | 1188.7808 | 35.0125 | 37.178 | 52.5188
24.3 | 1192.2727 | 34.9193 | 37.0789 | 52.3789
24.4 | 1195.7553 | 34.8263 | 36.98 | 52.2394
24.5 | 1199.2287 | 34.7335 | 36.8814 | 52.1003
24.6 | 1202.6928 | 34.641 | 36.7831 | 51.9615
24.7 | 1206.1477 | 34.5488 | 36.685 | 51.8232
24.8 | 1209.5934 | 34.4568 | 36.5872 | 51.6851
24.9 | 1213.0299 | 34.365 | 36.4897 | 51.5475
25 | 1216.4572 | 34.2735 | 36.3924 | 51.4102
25.1 | 1219.8754 | 34.1822 | 36.2954 | 51.2733
25.2 | 1223.2845 | 34.0912 | 36.1987 | 51.1368
25.3 | 1226.6846 | 34.0004 | 36.1022 | 51.0006
25.4 | 1230.0756 | 33.9098 | 36.006 | 50.8648
25.5 | 1233.4575 | 33.8195 | 35.91 | 50.7293
25.6 | 1236.8305 | 33.7295 | 35.8143 | 50.5942
25.7 | 1240.1944 | 33.6396 | 35.7189 | 50.4595
25.8 | 1243.5494 | 33.5501 | 35.6237 | 50.3251
25.9 | 1246.8955 | 33.4607 | 35.5288 | 50.1911
26 | 1250.2327 | 33.3716 | 35.4341 | 50.0574
26.1 | 1253.5609 | 33.2827 | 35.3397 | 49.9241
26.2 | 1256.8804 | 33.1941 | 35.2455 | 49.7911
26.3 | 1260.1909 | 33.1057 | 35.1516 | 49.6585
26.4 | 1263.4927 | 33.0175 | 35.058 | 49.5263
26.5 | 1266.7856 | 32.9296 | 34.9646 | 49.3944
26.6 | 1270.0698 | 32.8419 | 34.8714 | 49.2629
26.7 | 1273.3453 | 32.7544 | 34.7785 | 49.1317
26.8 | 1276.612 | 32.6672 | 34.6859 | 49.0008
26.9 | 1279.87 | 32.5802 | 34.5935 | 48.8703
27 | 1283.1194 | 32.4935 | 34.5013 | 48.7402
27.1 | 1286.3601 | 32.4069 | 34.4094 | 48.6104
27.2 | 1289.5921 | 32.3206 | 34.3178 | 48.4809
27.3 | 1292.8156 | 32.2345 | 34.2264 | 48.3518
27.4 | 1296.0304 | 32.1487 | 34.1352 | 48.2231
27.5 | 1299.2367 | 32.0631 | 34.0443 | 48.0946
27.6 | 1302.4345 | 31.9777 | 33.9536 | 47.9665
27.7 | 1305.6238 | 31.8925 | 33.8632 | 47.8388
27.8 | 1308.8045 | 31.8076 | 33.773 | 47.7114
27.9 | 1311.9768 | 31.7229 | 33.6831 | 47.5843
28 | 1315.1407 | 31.6384 | 33.5934 | 47.4576
28.1 | 1318.2961 | 31.5542 | 33.5039 | 47.3312
28.2 | 1321.4431 | 31.4701 | 33.4147 | 47.2052
28.3 | 1324.5817 | 31.3863 | 33.3257 | 47.0795
28.4 | 1327.712 | 31.3027 | 33.2369 | 46.9541
28.5 | 1330.8339 | 31.2194 | 33.1484 | 46.8291
28.6 | 1333.9476 | 31.1362 | 33.0601 | 46.7043
28.7 | 1337.0529 | 31.0533 | 32.9721 | 46.58
28.8 | 1340.1499 | 30.9706 | 32.8843 | 46.4559
28.9 | 1343.2388 | 30.8881 | 32.7967 | 46.3322
29 | 1346.3193 | 30.8059 | 32.7094 | 46.2088
29.1 | 1349.3917 | 30.7238 | 32.6223 | 46.0858
29.2 | 1352.4559 | 30.642 | 32.5354 | 45.963
29.3 | 1355.512 | 30.5604 | 32.4488 | 45.8406
29.4 | 1358.5599 | 30.479 | 32.3624 | 45.7185
29.5 | 1361.5997 | 30.3979 | 32.2762 | 45.5968
29.6 | 1364.6314 | 30.3169 | 32.1902 | 45.4754
29.7 | 1367.655 | 30.2362 | 32.1045 | 45.3542
29.8 | 1370.6705 | 30.1556 | 32.019 | 45.2335
29.9 | 1373.6781 | 30.0753 | 31.9338 | 45.113
30 | 1376.6776 | 29.9952 | 31.8487 | 44.9929
30.1 | 1379.6691 | 29.9154 | 31.7639 | 44.873
30.2 | 1382.6527 | 29.8357 | 31.6793 | 44.7535
30.3 | 1385.6283 | 29.7562 | 31.595 | 44.6344
30.4 | 1388.596 | 29.677 | 31.5108 | 44.5155
30.5 | 1391.5558 | 29.598 | 31.4269 | 44.3969
30.6 | 1394.5077 | 29.5191 | 31.3432 | 44.2787
30.7 | 1397.4518 | 29.4405 | 31.2598 | 44.1608
30.8 | 1400.388 | 29.3621 | 31.1765 | 44.0432
30.9 | 1403.3164 | 29.2839 | 31.0935 | 43.9259
31 | 1406.237 | 29.2059 | 31.0107 | 43.8089
31.1 | 1409.1498 | 29.1282 | 30.9281 | 43.6922
31.2 | 1412.0549 | 29.0506 | 30.8458 | 43.5759
31.3 | 1414.9522 | 28.9732 | 30.7636 | 43.4598
31.4 | 1417.8418 | 28.8961 | 30.6817 | 43.3441
31.5 | 1420.7237 | 28.8191 | 30.6 | 43.2287
31.6 | 1423.5979 | 28.7424 | 30.5185 | 43.1135
31.7 | 1426.4645 | 28.6658 | 30.4373 | 42.9987
31.8 | 1429.3235 | 28.5895 | 30.3562 | 42.8842
31.9 | 1432.1748 | 28.5133 | 30.2754 | 42.77
32 | 1435.0185 | 28.4374 | 30.1947 | 42.6561
32.1 | 1437.8547 | 28.3617 | 30.1143 | 42.5425
32.2 | 1440.6833 | 28.2861 | 30.0341 | 42.4292
32.3 | 1443.5044 | 28.2108 | 29.9542 | 42.3162
32.4 | 1446.318 | 28.1357 | 29.8744 | 42.2035
32.5 | 1449.124 | 28.0608 | 29.7948 | 42.0911
32.6 | 1451.9226 | 27.986 | 29.7155 | 41.979
32.7 | 1454.7138 | 27.9115 | 29.6364 | 41.8672
32.8 | 1457.4975 | 27.8372 | 29.5574 | 41.7557
32.9 | 1460.2738 | 27.763 | 29.4787 | 41.6445
33 | 1463.0427 | 27.6891 | 29.4002 | 41.5336
33.1 | 1465.8043 | 27.6154 | 29.3219 | 41.423
33.2 | 1468.5584 | 27.5418 | 29.2438 | 41.3127
33.3 | 1471.3053 | 27.4685 | 29.166 | 41.2027
33.4 | 1474.0448 | 27.3953 | 29.0883 | 41.093
33.5 | 1476.7771 | 27.3224 | 29.0108 | 40.9835
33.6 | 1479.502 | 27.2496 | 28.9336 | 40.8744
33.7 | 1482.2197 | 27.177 | 28.8565 | 40.7655
33.8 | 1484.9302 | 27.1047 | 28.7797 | 40.657
33.9 | 1487.6334 | 27.0325 | 28.703 | 40.5487
34 | 1490.3295 | 26.9605 | 28.6266 | 40.4407
34.1 | 1493.0183 | 26.8887 | 28.5504 | 40.333
34.2 | 1495.7 | 26.8171 | 28.4743 | 40.2256
34.3 | 1498.3746 | 26.7457 | 28.3985 | 40.1185
34.4 | 1501.0421 | 26.6744 | 28.3229 | 40.0116
34.5 | 1503.7024 | 26.6034 | 28.2474 | 39.9051
34.6 | 1506.3557 | 26.5325 | 28.1722 | 39.7988
34.7 | 1509.0018 | 26.4619 | 28.0972 | 39.6928
34.8 | 1511.641 | 26.3914 | 28.0224 | 39.5871
34.9 | 1514.2731 | 26.3211 | 27.9477 | 39.4817
35 | 1516.8982 | 26.251 | 27.8733 | 39.3766
35.1 | 1519.5163 | 26.1811 | 27.7991 | 39.2717
35.2 | 1522.1275 | 26.1114 | 27.725 | 39.1671
35.3 | 1524.7316 | 26.0419 | 27.6512 | 39.0628
35.4 | 1527.3289 | 25.9725 | 27.5776 | 38.9588
35.5 | 1529.9192 | 25.9033 | 27.5041 | 38.855
35.6 | 1532.5027 | 25.8344 | 27.4309 | 38.7515
35.7 | 1535.0792 | 25.7656 | 27.3578 | 38.6483
35.8 | 1537.6489 | 25.6969 | 27.285 | 38.5454
35.9 | 1540.2118 | 25.6285 | 27.2123 | 38.4428
36 | 1542.7678 | 25.5603 | 27.1398 | 38.3404
36.1 | 1545.317 | 25.4922 | 27.0676 | 38.2383
36.2 | 1547.8594 | 25.4243 | 26.9955 | 38.1364
36.3 | 1550.3951 | 25.3566 | 26.9236 | 38.0349
36.4 | 1552.924 | 25.2891 | 26.8519 | 37.9336
36.5 | 1555.4462 | 25.2217 | 26.7804 | 37.8326
36.6 | 1557.9616 | 25.1545 | 26.7091 | 37.7318
36.7 | 1560.4704 | 25.0876 | 26.6379 | 37.6313
36.8 | 1562.9725 | 25.0207 | 26.567 | 37.5311
36.9 | 1565.4679 | 24.9541 | 26.4962 | 37.4312
37 | 1567.9566 | 24.8877 | 26.4257 | 37.3315
37.1 | 1570.4388 | 24.8214 | 26.3553 | 37.2321
37.2 | 1572.9143 | 24.7553 | 26.2851 | 37.1329
37.3 | 1575.3832 | 24.6894 | 26.2151 | 37.034
37.4 | 1577.8456 | 24.6236 | 26.1453 | 36.9354
37.5 | 1580.3014 | 24.558 | 26.0757 | 36.837
37.6 | 1582.7507 | 24.4926 | 26.0062 | 36.7389
37.7 | 1585.1934 | 24.4274 | 25.937 | 36.6411
37.8 | 1587.6296 | 24.3623 | 25.8679 | 36.5435
37.9 | 1590.0594 | 24.2975 | 25.799 | 36.4462
38 | 1592.4827 | 24.2328 | 25.7303 | 36.3491
38.1 | 1594.8995 | 24.1682 | 25.6618 | 36.2523
38.2 | 1597.3099 | 24.1039 | 25.5934 | 36.1558
38.3 | 1599.7138 | 24.0397 | 25.5253 | 36.0595
38.4 | 1602.1114 | 23.9756 | 25.4573 | 35.9635
38.5 | 1604.5026 | 23.9118 | 25.3895 | 35.8677
38.6 | 1606.8874 | 23.8481 | 25.3219 | 35.7722
38.7 | 1609.2658 | 23.7846 | 25.2545 | 35.6769
38.8 | 1611.638 | 23.7213 | 25.1872 | 35.5819
38.9 | 1614.0038 | 23.6581 | 25.1201 | 35.4871
39 | 1616.3633 | 23.5951 | 25.0532 | 35.3926
39.1 | 1618.7165 | 23.5323 | 24.9865 | 35.2984
39.2 | 1621.0635 | 23.4696 | 24.92 | 35.2044
39.3 | 1623.4042 | 23.4071 | 24.8536 | 35.1106
39.4 | 1625.7387 | 23.3447 | 24.7874 | 35.0171
39.5 | 1628.0669 | 23.2826 | 24.7214 | 34.9239
39.6 | 1630.389 | 23.2206 | 24.6556 | 34.8309
39.7 | 1632.7049 | 23.1587 | 24.5899 | 34.7381
39.8 | 1635.0146 | 23.0971 | 24.5244 | 34.6456
39.9 | 1637.3181 | 23.0356 | 24.4591 | 34.5533
40 | 1639.6155 | 22.9742 | 24.394 | 34.4613
40.1 | 1641.9068 | 22.913 | 24.329 | 34.3695
40.2 | 1644.192 | 22.852 | 24.2642 | 34.278
40.3 | 1646.4711 | 22.7911 | 24.1996 | 34.1867
40.4 | 1648.7442 | 22.7304 | 24.1351 | 34.0957
40.5 | 1651.0112 | 22.6699 | 24.0709 | 34.0049
40.6 | 1653.2721 | 22.6095 | 24.0068 | 33.9143
40.7 | 1655.5271 | 22.5493 | 23.9428 | 33.824
40.8 | 1657.776 | 22.4893 | 23.8791 | 33.7339
40.9 | 1660.0189 | 22.4294 | 23.8155 | 33.6441
41 | 1662.2559 | 22.3697 | 23.7521 | 33.5545
41.1 | 1664.4869 | 22.3101 | 23.6888 | 33.4651
41.2 | 1666.712 | 22.2507 | 23.6257 | 33.376
41.3 | 1668.9311 | 22.1914 | 23.5628 | 33.2871
41.4 | 1671.1444 | 22.1323 | 23.5 | 33.1985
41.5 | 1673.3517 | 22.0734 | 23.4375 | 33.1101
41.6 | 1675.5531 | 22.0146 | 23.375 | 33.0219
41.7 | 1677.7487 | 21.956 | 23.3128 | 32.9339
41.8 | 1679.9385 | 21.8975 | 23.2507 | 32.8462
41.9 | 1682.1224 | 21.8392 | 23.1888 | 32.7588
42 | 1684.3005 | 21.781 | 23.127 | 32.6715
42.1 | 1686.4728 | 21.723 | 23.0654 | 32.5845
42.2 | 1688.6393 | 21.6652 | 23.004 | 32.4977
42.3 | 1690.8001 | 21.6075 | 22.9428 | 32.4112
42.4 | 1692.9551 | 21.5499 | 22.8817 | 32.3249
42.5 | 1695.1043 | 21.4925 | 22.8207 | 32.2388
42.6 | 1697.2479 | 21.4353 | 22.7599 | 32.1529
42.7 | 1699.3857 | 21.3782 | 22.6993 | 32.0673
42.8 | 1701.5178 | 21.3213 | 22.6389 | 31.9819
42.9 | 1703.6442 | 21.2645 | 22.5786 | 31.8967
43 | 1705.765 | 21.2079 | 22.5185 | 31.8118
43.1 | 1707.8802 | 21.1514 | 22.4585 | 31.7271
43.2 | 1709.9897 | 21.0951 | 22.3987 | 31.6426
43.3 | 1712.0936 | 21.0389 | 22.339 | 31.5583
43.4 | 1714.1919 | 20.9828 | 22.2795 | 31.4743
43.5 | 1716.2845 | 20.927 | 22.2202 | 31.3905
43.6 | 1718.3717 | 20.8712 | 22.161 | 31.3069
43.7 | 1720.4532 | 20.8157 | 22.102 | 31.2235
43.8 | 1722.5293 | 20.7602 | 22.0432 | 31.1403
43.9 | 1724.5998 | 20.7049 | 21.9845 | 31.0574
44 | 1726.6647 | 20.6498 | 21.9259 | 30.9747
44.1 | 1728.7242 | 20.5948 | 21.8675 | 30.8922
44.2 | 1730.7782 | 20.54 | 21.8093 | 30.8099
44.3 | 1732.8267 | 20.4853 | 21.7512 | 30.7279
44.4 | 1734.8698 | 20.4307 | 21.6933 | 30.6461
44.5 | 1736.9074 | 20.3763 | 21.6355 | 30.5644
44.6 | 1738.9396 | 20.322 | 21.5779 | 30.483
44.7 | 1740.9664 | 20.2679 | 21.5204 | 30.4019
44.8 | 1742.9878 | 20.2139 | 21.4631 | 30.3209
44.9 | 1745.0038 | 20.1601 | 21.406 | 30.2401
45 | 1747.0145 | 20.1064 | 21.3489 | 30.1596
45.1 | 1749.0198 | 20.0529 | 21.2921 | 30.0793
45.2 | 1751.0197 | 19.9995 | 21.2354 | 29.9992
45.3 | 1753.0143 | 19.9462 | 21.1788 | 29.9193
45.4 | 1755.0036 | 19.8931 | 21.1224 | 29.8396
45.5 | 1756.9876 | 19.8401 | 21.0662 | 29.7602
45.6 | 1758.9664 | 19.7873 | 21.0101 | 29.6809
45.7 | 1760.9398 | 19.7346 | 20.9541 | 29.6019
45.8 | 1762.908 | 19.682 | 20.8983 | 29.523
45.9 | 1764.871 | 19.6296 | 20.8427 | 29.4444
46 | 1766.8287 | 19.5773 | 20.7872 | 29.366
46.1 | 1768.7812 | 19.5252 | 20.7318 | 29.2878
46.2 | 1770.7286 | 19.4732 | 20.6766 | 29.2098
46.3 | 1772.6707 | 19.4213 | 20.6215 | 29.132
46.4 | 1774.6077 | 19.3696 | 20.5666 | 29.0544
46.5 | 1776.5395 | 19.318 | 20.5118 | 28.977
46.6 | 1778.4661 | 19.2666 | 20.4572 | 28.8999
46.7 | 1780.3876 | 19.2153 | 20.4027 | 28.8229
46.8 | 1782.3041 | 19.1641 | 20.3484 | 28.7461
46.9 | 1784.2154 | 19.1131 | 20.2942 | 28.6696
47 | 1786.1216 | 19.0622 | 20.2402 | 28.5932
47.1 | 1788.0227 | 19.0114 | 20.1863 | 28.5171
47.2 | 1789.9188 | 18.9608 | 20.1325 | 28.4412
47.3 | 1791.8098 | 18.9103 | 20.0789 | 28.3654
47.4 | 1793.6958 | 18.8599 | 20.0254 | 28.2899
47.5 | 1795.5768 | 18.8097 | 19.9721 | 28.2145
47.6 | 1797.4527 | 18.7596 | 19.9189 | 28.1394
47.7 | 1799.3237 | 18.7096 | 19.8659 | 28.0645
47.8 | 1801.1897 | 18.6598 | 19.8129 | 27.9897
47.9 | 1803.0507 | 18.6101 | 19.7602 | 27.9152
48 | 1804.9067 | 18.5606 | 19.7076 | 27.8408
48.1 | 1806.7579 | 18.5111 | 19.6551 | 27.7667
48.2 | 1808.604 | 18.4618 | 19.6027 | 27.6927
48.3 | 1810.4453 | 18.4127 | 19.5505 | 27.619
48.4 | 1812.2817 | 18.3636 | 19.4985 | 27.5454
48.5 | 1814.1131 | 18.3147 | 19.4465 | 27.4721
48.6 | 1815.9397 | 18.266 | 19.3947 | 27.3989
48.7 | 1817.7615 | 18.2173 | 19.3431 | 27.326
48.8 | 1819.5784 | 18.1688 | 19.2916 | 27.2532
48.9 | 1821.3904 | 18.1204 | 19.2402 | 27.1806
49 | 1823.1976 | 18.0721 | 19.189 | 27.1082
49.1 | 1825 | 18.024 | 19.1379 | 27.036
49.2 | 1826.7976 | 17.976 | 19.0869 | 26.964
49.3 | 1828.5904 | 17.9281 | 19.0361 | 26.8922
49.4 | 1830.3785 | 17.8804 | 18.9854 | 26.8206
49.5 | 1832.1617 | 17.8328 | 18.9348 | 26.7492
49.6 | 1833.9403 | 17.7853 | 18.8844 | 26.6779
49.7 | 1835.7141 | 17.7379 | 18.8341 | 26.6069
49.8 | 1837.4831 | 17.6907 | 18.7839 | 26.536
49.9 | 1839.2475 | 17.6436 | 18.7339 | 26.4654
50 | 1841.0072 | 17.5966 | 18.684 | 26.3949
50.1 | 1842.7621 | 17.5497 | 18.6343 | 26.3246
50.2 | 1844.5124 | 17.503 | 18.5846 | 26.2545
50.3 | 1846.2581 | 17.4564 | 18.5352 | 26.1846
50.4 | 1847.9991 | 17.4099 | 18.4858 | 26.1148
50.5 | 1849.7354 | 17.3635 | 18.4366 | 26.0453
50.6 | 1851.4671 | 17.3173 | 18.3875 | 25.9759
50.7 | 1853.1943 | 17.2712 | 18.3385 | 25.9068
50.8 | 1854.9168 | 17.2252 | 18.2897 | 25.8378
50.9 | 1856.6347 | 17.1793 | 18.2409 | 25.769
51 | 1858.3481 | 17.1336 | 18.1924 | 25.7003
51.1 | 1860.0569 | 17.0879 | 18.1439 | 25.6319
51.2 | 1861.7611 | 17.0424 | 18.0956 | 25.5636
51.3 | 1863.4608 | 16.997 | 18.0474 | 25.4955
51.4 | 1865.156 | 16.9518 | 17.9994 | 25.4276
51.5 | 1866.8466 | 16.9066 | 17.9514 | 25.3599
51.6 | 1868.5328 | 16.8616 | 17.9036 | 25.2924
51.7 | 1870.2145 | 16.8167 | 17.8559 | 25.225
51.8 | 1871.8917 | 16.7719 | 17.8084 | 25.1579
51.9 | 1873.5644 | 16.7272 | 17.761 | 25.0909
52 | 1875.2326 | 16.6827 | 17.7137 | 25.024
52.1 | 1876.8965 | 16.6383 | 17.6665 | 24.9574
52.2 | 1878.5559 | 16.594 | 17.6194 | 24.8909
52.3 | 1880.2108 | 16.5498 | 17.5725 | 24.8247
52.4 | 1881.8614 | 16.5057 | 17.5257 | 24.7585
52.5 | 1883.5076 | 16.4617 | 17.479 | 24.6926
52.6 | 1885.1494 | 16.4179 | 17.4325 | 24.6268
52.7 | 1886.7868 | 16.3742 | 17.3861 | 24.5613
52.8 | 1888.4199 | 16.3306 | 17.3398 | 24.4959
52.9 | 1890.0486 | 16.2871 | 17.2936 | 24.4306
53 | 1891.6729 | 16.2437 | 17.2475 | 24.3656
53.1 | 1893.293 | 16.2004 | 17.2016 | 24.3007
53.2 | 1894.9087 | 16.1573 | 17.1558 | 24.236
53.3 | 1896.5201 | 16.1143 | 17.1101 | 24.1714
53.4 | 1898.1273 | 16.0714 | 17.0645 | 24.107
53.5 | 1899.7301 | 16.0286 | 17.0191 | 24.0428
53.6 | 1901.3287 | 15.9859 | 16.9738 | 23.9788
53.7 | 1902.923 | 15.9433 | 16.9286 | 23.915
53.8 | 1904.5131 | 15.9008 | 16.8835 | 23.8513
53.9 | 1906.099 | 15.8585 | 16.8385 | 23.7877
54 | 1907.6806 | 15.8163 | 16.7937 | 23.7244
54.1 | 1909.258 | 15.7741 | 16.749 | 23.6612
54.2 | 1910.8312 | 15.7321 | 16.7043 | 23.5982
54.3 | 1912.4003 | 15.6902 | 16.6599 | 23.5354
54.4 | 1913.9651 | 15.6485 | 16.6155 | 23.4727
54.5 | 1915.5258 | 15.6068 | 16.5712 | 23.4102
54.6 | 1917.0823 | 15.5652 | 16.5271 | 23.3478
54.7 | 1918.6347 | 15.5238 | 16.4831 | 23.2856
54.8 | 1920.1829 | 15.4824 | 16.4392 | 23.2236
54.9 | 1921.727 | 15.4412 | 16.3954 | 23.1618
55 | 1923.267 | 15.4001 | 16.3518 | 23.1001
55.1 | 1924.803 | 15.3591 | 16.3082 | 23.0386
55.2 | 1926.3348 | 15.3182 | 16.2648 | 22.9772
55.3 | 1927.8625 | 15.2774 | 16.2215 | 22.916
55.4 | 1929.3862 | 15.2367 | 16.1783 | 22.855
55.5 | 1930.9058 | 15.1961 | 16.1352 | 22.7941
55.6 | 1932.4213 | 15.1556 | 16.0922 | 22.7334
55.7 | 1933.9329 | 15.1153 | 16.0494 | 22.6729
55.8 | 1935.4404 | 15.075 | 16.0066 | 22.6125
55.9 | 1936.9439 | 15.0349 | 15.964 | 22.5523
56 | 1938.4433 | 14.9948 | 15.9215 | 22.4922
56.1 | 1939.9388 | 14.9549 | 15.8791 | 22.4323
56.2 | 1941.4303 | 14.9151 | 15.8368 | 22.3726
56.3 | 1942.9179 | 14.8753 | 15.7946 | 22.313
56.4 | 1944.4014 | 14.8357 | 15.7526 | 22.2536
56.5 | 1945.8811 | 14.7962 | 15.7106 | 22.1943
56.6 | 1947.3567 | 14.7568 | 15.6688 | 22.1352
56.7 | 1948.8285 | 14.7175 | 15.627 | 22.0763
56.8 | 1950.2963 | 14.6783 | 15.5854 | 22.0175
56.9 | 1951.7603 | 14.6392 | 15.5439 | 21.9589
57 | 1953.2203 | 14.6003 | 15.5025 | 21.9004
57.1 | 1954.6764 | 14.5614 | 15.4612 | 21.8421
57.2 | 1956.1287 | 14.5226 | 15.4201 | 21.7839
57.3 | 1957.5771 | 14.4839 | 15.379 | 21.7259
57.4 | 1959.0216 | 14.4453 | 15.338 | 21.668
57.5 | 1960.4623 | 14.4069 | 15.2972 | 21.6103
57.6 | 1961.8991 | 14.3685 | 15.2564 | 21.5528
57.7 | 1963.3322 | 14.3302 | 15.2158 | 21.4954
57.8 | 1964.7614 | 14.2921 | 15.1753 | 21.4381
57.9 | 1966.1868 | 14.254 | 15.1349 | 21.381
58 | 1967.6084 | 14.2161 | 15.0946 | 21.3241
58.1 | 1969.0262 | 14.1782 | 15.0544 | 21.2673
58.2 | 1970.4402 | 14.1404 | 15.0143 | 21.2107
58.3 | 1971.8505 | 14.1028 | 14.9743 | 21.1542
58.4 | 1973.257 | 14.0652 | 14.9344 | 21.0978
58.5 | 1974.6598 | 14.0278 | 14.8947 | 21.0417
58.6 | 1976.0589 | 13.9904 | 14.855 | 20.9856
58.7 | 1977.4542 | 13.9532 | 14.8154 | 20.9297
58.8 | 1978.8458 | 13.916 | 14.776 | 20.874
58.9 | 1980.2337 | 13.8789 | 14.7366 | 20.8184
59 | 1981.6179 | 13.842 | 14.6974 | 20.763
59.1 | 1982.9984 | 13.8051 | 14.6582 | 20.7077
59.2 | 1984.3752 | 13.7683 | 14.6192 | 20.6525
59.3 | 1985.7484 | 13.7317 | 14.5803 | 20.5975
59.4 | 1987.1179 | 13.6951 | 14.5414 | 20.5427
59.5 | 1988.4838 | 13.6586 | 14.5027 | 20.488
59.6 | 1989.846 | 13.6223 | 14.4641 | 20.4334
59.7 | 1991.2046 | 13.586 | 14.4256 | 20.379
59.8 | 1992.5596 | 13.5498 | 14.3872 | 20.3247
59.9 | 1993.9109 | 13.5137 | 14.3488 | 20.2706
60 | 1995.2587 | 13.4777 | 14.3106 | 20.2166
60.1 | 1996.6029 | 13.4418 | 14.2725 | 20.1628
60.2 | 1997.9435 | 13.406 | 14.2345 | 20.1091
60.3 | 1999.2805 | 13.3703 | 14.1966 | 20.0555
60.4 | 2000.614 | 13.3347 | 14.1588 | 20.0021
60.5 | 2001.9439 | 13.2992 | 14.1211 | 19.9488
60.6 | 2003.2703 | 13.2638 | 14.0835 | 19.8957
60.7 | 2004.5931 | 13.2285 | 14.046 | 19.8427
60.8 | 2005.9125 | 13.1933 | 14.0086 | 19.7899
60.9 | 2007.2283 | 13.1581 | 13.9713 | 19.7372
61 | 2008.5406 | 13.1231 | 13.9341 | 19.6846
61.1 | 2009.8494 | 13.0881 | 13.8969 | 19.6322
61.2 | 2011.1547 | 13.0533 | 13.8599 | 19.5799
61.3 | 2012.4566 | 13.0185 | 13.823 | 19.5278
61.4 | 2013.755 | 12.9838 | 13.7862 | 19.4758
61.5 | 2015.0499 | 12.9493 | 13.7495 | 19.4239
61.6 | 2016.3414 | 12.9148 | 13.7129 | 19.3722
61.7 | 2017.6294 | 12.8804 | 13.6764 | 19.3206
61.8 | 2018.914 | 12.8461 | 13.6399 | 19.2691
61.9 | 2020.1952 | 12.8119 | 13.6036 | 19.2178
62 | 2021.473 | 12.7777 | 13.5674 | 19.1666
62.1 | 2022.7474 | 12.7437 | 13.5313 | 19.1156
62.2 | 2024.0183 | 12.7098 | 13.4952 | 19.0647
62.3 | 2025.2859 | 12.6759 | 13.4593 | 19.0139
62.4 | 2026.5501 | 12.6422 | 13.4234 | 18.9633
62.5 | 2027.811 | 12.6085 | 13.3877 | 18.9128
62.6 | 2029.0685 | 12.5749 | 13.352 | 18.8624
62.7 | 2030.3226 | 12.5414 | 13.3165 | 18.8122
62.8 | 2031.5734 | 12.508 | 13.281 | 18.7621
62.9 | 2032.8209 | 12.4747 | 13.2456 | 18.7121
63 | 2034.0651 | 12.4415 | 13.2104 | 18.6623
63.1 | 2035.3059 | 12.4084 | 13.1752 | 18.6126
63.2 | 2036.5434 | 12.3753 | 13.1401 | 18.563
63.3 | 2037.7777 | 12.3424 | 13.1051 | 18.5136
63.4 | 2039.0086 | 12.3095 | 13.0702 | 18.4643
63.5 | 2040.2363 | 12.2767 | 13.0354 | 18.4151
63.6 | 2041.4607 | 12.244 | 13.0007 | 18.366
63.7 | 2042.6818 | 12.2114 | 12.9661 | 18.3171
63.8 | 2043.8997 | 12.1789 | 12.9315 | 18.2684
63.9 | 2045.1144 | 12.1465 | 12.8971 | 18.2197
64 | 2046.3258 | 12.1141 | 12.8628 | 18.1712
64.1 | 2047.534 | 12.0819 | 12.8285 | 18.1228
64.2 | 2048.7389 | 12.0497 | 12.7943 | 18.0745
64.3 | 2049.9407 | 12.0176 | 12.7603 | 18.0264
64.4 | 2051.1393 | 11.9856 | 12.7263 | 17.9784
64.5 | 2052.3346 | 11.9537 | 12.6924 | 17.9305
64.6 | 2053.5268 | 11.9218 | 12.6586 | 17.8828
64.7 | 2054.7158 | 11.8901 | 12.6249 | 17.8351
64.8 | 2055.9017 | 11.8584 | 12.5913 | 17.7876
64.9 | 2057.0844 | 11.8268 | 12.5577 | 17.7403
65 | 2058.2639 | 11.7953 | 12.5243 | 17.693
65.1 | 2059.4403 | 11.7639 | 12.4909 | 17.6459
65.2 | 2060.6135 | 11.7326 | 12.4577 | 17.5989
65.3 | 2061.7837 | 11.7014 | 12.4245 | 17.552
65.4 | 2062.9507 | 11.6702 | 12.3914 | 17.5053
65.5 | 2064.1146 | 11.6391 | 12.3584 | 17.4587
65.6 | 2065.2754 | 11.6081 | 12.3255 | 17.4122
65.7 | 2066.4331 | 11.5772 | 12.2927 | 17.3658
65.8 | 2067.5878 | 11.5464 | 12.2599 | 17.3196
65.9 | 2068.7393 | 11.5156 | 12.2273 | 17.2734
66 | 2069.8878 | 11.485 | 12.1947 | 17.2274
66.1 | 2071.0333 | 11.4544 | 12.1622 | 17.1816
66.2 | 2072.1757 | 11.4239 | 12.1298 | 17.1358
66.3 | 2073.315 | 11.3935 | 12.0975 | 17.0902
66.4 | 2074.4513 | 11.3631 | 12.0653 | 17.0447
66.5 | 2075.5846 | 11.3328 | 12.0332 | 16.9993
66.6 | 2076.7149 | 11.3027 | 12.0011 | 16.954
66.7 | 2077.8421 | 11.2726 | 11.9692 | 16.9088
66.8 | 2078.9664 | 11.2425 | 11.9373 | 16.8638
66.9 | 2080.0876 | 11.2126 | 11.9055 | 16.8189
67 | 2081.2059 | 11.1827 | 11.8738 | 16.7741
67.1 | 2082.3212 | 11.153 | 11.8422 | 16.7294
67.2 | 2083.4335 | 11.1233 | 11.8107 | 16.6849
67.3 | 2084.5429 | 11.0936 | 11.7792 | 16.6405
67.4 | 2085.6493 | 11.0641 | 11.7478 | 16.5961
67.5 | 2086.7528 | 11.0346 | 11.7165 | 16.5519
67.6 | 2087.8533 | 11.0052 | 11.6853 | 16.5079
67.7 | 2088.9509 | 10.9759 | 11.6542 | 16.4639
67.8 | 2090.0456 | 10.9467 | 11.6232 | 16.4201
67.9 | 2091.1373 | 10.9176 | 11.5922 | 16.3763
68 | 2092.2262 | 10.8885 | 11.5614 | 16.3327
68.1 | 2093.3121 | 10.8595 | 11.5306 | 16.2892
68.2 | 2094.3952 | 10.8306 | 11.4999 | 16.2458
68.3 | 2095.4753 | 10.8017 | 11.4692 | 16.2026
68.4 | 2096.5526 | 10.773 | 11.4387 | 16.1594
68.5 | 2097.6271 | 10.7443 | 11.4082 | 16.1164
68.6 | 2098.6986 | 10.7157 | 11.3779 | 16.0735
68.7 | 2099.7673 | 10.6871 | 11.3476 | 16.0307
68.8 | 2100.8332 | 10.6587 | 11.3173 | 15.988
68.9 | 2101.8962 | 10.6303 | 11.2872 | 15.9454
69 | 2102.9564 | 10.602 | 11.2571 | 15.9029
69.1 | 2104.0138 | 10.5737 | 11.2272 | 15.8606
69.2 | 2105.0684 | 10.5456 | 11.1973 | 15.8183
69.3 | 2106.1201 | 10.5175 | 11.1674 | 15.7762
69.4 | 2107.1691 | 10.4895 | 11.1377 | 15.7342
69.5 | 2108.2152 | 10.4615 | 11.108 | 15.6923
69.6 | 2109.2586 | 10.4337 | 11.0785 | 15.6505
69.7 | 2110.2992 | 10.4059 | 11.049 | 15.6088
69.8 | 2111.337 | 10.3782 | 11.0195 | 15.5673
69.9 | 2112.372 | 10.3505 | 10.9902 | 15.5258
70 | 2113.4043 | 10.323 | 10.9609 | 15.4845
70.1 | 2114.4339 | 10.2955 | 10.9317 | 15.4432
70.2 | 2115.4607 | 10.2681 | 10.9026 | 15.4021
70.3 | 2116.4848 | 10.2407 | 10.8736 | 15.3611
70.4 | 2117.5061 | 10.2134 | 10.8446 | 15.3202
70.5 | 2118.5247 | 10.1862 | 10.8157 | 15.2794
70.6 | 2119.5406 | 10.1591 | 10.7869 | 15.2387
70.7 | 2120.5539 | 10.1321 | 10.7582 | 15.1981
70.8 | 2121.5644 | 10.1051 | 10.7296 | 15.1576
70.9 | 2122.5722 | 10.0782 | 10.701 | 15.1173
71 | 2123.5773 | 10.0513 | 10.6725 | 15.077
71.1 | 2124.5798 | 10.0246 | 10.6441 | 15.0368
71.2 | 2125.5796 | 9.9979 | 10.6157 | 14.9968
71.3 | 2126.5767 | 9.9712 | 10.5874 | 14.9569
71.4 | 2127.5712 | 9.9447 | 10.5593 | 14.917
71.5 | 2128.563 | 9.9182 | 10.5311 | 14.8773
71.6 | 2129.5522 | 9.8918 | 10.5031 | 14.8377
71.7 | 2130.5387 | 9.8654 | 10.4751 | 14.7982
71.8 | 2131.5226 | 9.8392 | 10.4472 | 14.7588
71.9 | 2132.5039 | 9.813 | 10.4194 | 14.7195
72 | 2133.4826 | 9.7868 | 10.3916 | 14.6803
72.1 | 2134.4587 | 9.7608 | 10.364 | 14.6412
72.2 | 2135.4322 | 9.7348 | 10.3364 | 14.6022
72.3 | 2136.403 | 9.7089 | 10.3088 | 14.5633
72.4 | 2137.3713 | 9.683 | 10.2814 | 14.5245
72.5 | 2138.3371 | 9.6572 | 10.254 | 14.4858
72.6 | 2139.3002 | 9.6315 | 10.2267 | 14.4472
72.7 | 2140.2608 | 9.6058 | 10.1995 | 14.4088
72.8 | 2141.2188 | 9.5803 | 10.1723 | 14.3704
72.9 | 2142.1743 | 9.5548 | 10.1452 | 14.3321
73 | 2143.1272 | 9.5293 | 10.1182 | 14.294
73.1 | 2144.0776 | 9.5039 | 10.0913 | 14.2559
73.2 | 2145.0255 | 9.4786 | 10.0644 | 14.2179
73.3 | 2145.9708 | 9.4534 | 10.0376 | 14.1801
73.4 | 2146.9136 | 9.4282 | 10.0108 | 14.1423
73.5 | 2147.8539 | 9.4031 | 9.9842 | 14.1046
73.6 | 2148.7918 | 9.3781 | 9.9576 | 14.0671
73.7 | 2149.7271 | 9.3531 | 9.9311 | 14.0296
73.8 | 2150.6599 | 9.3282 | 9.9046 | 13.9923
73.9 | 2151.5902 | 9.3033 | 9.8783 | 13.955
74 | 2152.5181 | 9.2786 | 9.8519 | 13.9178
74.1 | 2153.4434 | 9.2538 | 9.8257 | 13.8808
74.2 | 2154.3664 | 9.2292 | 9.7995 | 13.8438
74.3 | 2155.2868 | 9.2046 | 9.7734 | 13.8069
74.4 | 2156.2048 | 9.1801 | 9.7474 | 13.7702
74.5 | 2157.1204 | 9.1557 | 9.7215 | 13.7335
74.6 | 2158.0335 | 9.1313 | 9.6956 | 13.6969
74.7 | 2158.9442 | 9.107 | 9.6697 | 13.6604
74.8 | 2159.8525 | 9.0827 | 9.644 | 13.6241
74.9 | 2160.7584 | 9.0585 | 9.6183 | 13.5878
75 | 2161.6618 | 9.0344 | 9.5927 | 13.5516
75.1 | 2162.5628 | 9.0103 | 9.5672 | 13.5155
75.2 | 2163.4615 | 8.9863 | 9.5417 | 13.4795
75.3 | 2164.3577 | 8.9624 | 9.5163 | 13.4436
75.4 | 2165.2516 | 8.9385 | 9.4909 | 13.4078
75.5 | 2166.143 | 8.9147 | 9.4656 | 13.3721
75.6 | 2167.0321 | 8.891 | 9.4404 | 13.3365
75.7 | 2167.9189 | 8.8673 | 9.4153 | 13.301
75.8 | 2168.8032 | 8.8437 | 9.3902 | 13.2656
75.9 | 2169.6852 | 8.8201 | 9.3652 | 13.2302
76 | 2170.5649 | 8.7967 | 9.3403 | 13.195
76.1 | 2171.4422 | 8.7732 | 9.3154 | 13.1598
76.2 | 2172.3172 | 8.7499 | 9.2906 | 13.1248
76.3 | 2173.1899 | 8.7266 | 9.2659 | 13.0899
76.4 | 2174.0602 | 8.7033 | 9.2412 | 13.055
76.5 | 2174.9282 | 8.6801 | 9.2166 | 13.0202
76.6 | 2175.7939 | 8.657 | 9.192 | 12.9855
76.7 | 2176.6573 | 8.634 | 9.1675 | 12.951
76.8 | 2177.5184 | 8.611 | 9.1431 | 12.9165
76.9 | 2178.3772 | 8.5881 | 9.1188 | 12.8821
77 | 2179.2337 | 8.5652 | 9.0945 | 12.8478
77.1 | 2180.088 | 8.5424 | 9.0703 | 12.8136
77.2 | 2180.9399 | 8.5196 | 9.0461 | 12.7794
77.3 | 2181.7896 | 8.4969 | 9.022 | 12.7454
77.4 | 2182.6371 | 8.4743 | 8.998 | 12.7115
77.5 | 2183.4822 | 8.4517 | 8.974 | 12.6776
77.6 | 2184.3252 | 8.4292 | 8.9501 | 12.6438
77.7 | 2185.1658 | 8.4068 | 8.9263 | 12.6102
77.8 | 2186.0043 | 8.3844 | 8.9025 | 12.5766
77.9 | 2186.8405 | 8.3621 | 8.8788 | 12.5431
78 | 2187.6745 | 8.3398 | 8.8552 | 12.5097
78.1 | 2188.5062 | 8.3176 | 8.8316 | 12.4764
78.2 | 2189.3358 | 8.2954 | 8.8081 | 12.4432
78.3 | 2190.1631 | 8.2733 | 8.7846 | 12.41
78.4 | 2190.9882 | 8.2513 | 8.7612 | 12.377
78.5 | 2191.8112 | 8.2293 | 8.7379 | 12.344
78.6 | 2192.6319 | 8.2074 | 8.7146 | 12.3111
78.7 | 2193.4505 | 8.1856 | 8.6914 | 12.2783
78.8 | 2194.2668 | 8.1638 | 8.6683 | 12.2456
78.9 | 2195.081 | 8.142 | 8.6452 | 12.213
79 | 2195.8931 | 8.1203 | 8.6222 | 12.1805
79.1 | 2196.703 | 8.0987 | 8.5992 | 12.1481
79.2 | 2197.5107 | 8.0771 | 8.5763 | 12.1157
79.3 | 2198.3162 | 8.0556 | 8.5535 | 12.0835
79.4 | 2199.1196 | 8.0342 | 8.5307 | 12.0513
79.5 | 2199.9209 | 8.0128 | 8.508 | 12.0192
79.6 | 2200.7201 | 7.9914 | 8.4853 | 11.9872
79.7 | 2201.5171 | 7.9702 | 8.4627 | 11.9552
79.8 | 2202.312 | 7.9489 | 8.4402 | 11.9234
79.9 | 2203.1048 | 7.9278 | 8.4177 | 11.8917
80 | 2203.8954 | 7.9067 | 8.3953 | 11.86
80.1 | 2204.684 | 7.8856 | 8.3729 | 11.8284
80.2 | 2205.4704 | 7.8646 | 8.3506 | 11.7969
80.3 | 2206.2548 | 7.8437 | 8.3284 | 11.7655
80.4 | 2207.0371 | 7.8228 | 8.3062 | 11.7342
80.5 | 2207.8173 | 7.8019 | 8.2841 | 11.7029
80.6 | 2208.5954 | 7.7812 | 8.262 | 11.6717
80.7 | 2209.3714 | 7.7604 | 8.24 | 11.6407
80.8 | 2210.1454 | 7.7398 | 8.2181 | 11.6097
80.9 | 2210.9173 | 7.7192 | 8.1962 | 11.5787
81 | 2211.6872 | 7.6986 | 8.1744 | 11.5479
81.1 | 2212.455 | 7.6781 | 8.1526 | 11.5171
81.2 | 2213.2208 | 7.6577 | 8.1309 | 11.4865
81.3 | 2213.9845 | 7.6373 | 8.1092 | 11.4559
81.4 | 2214.7462 | 7.6169 | 8.0876 | 11.4254
81.5 | 2215.5059 | 7.5966 | 8.0661 | 11.395
81.6 | 2216.2635 | 7.5764 | 8.0446 | 11.3646
81.7 | 2217.0191 | 7.5562 | 8.0232 | 11.3343
81.8 | 2217.7727 | 7.5361 | 8.0018 | 11.3042
81.9 | 2218.5243 | 7.516 | 7.9805 | 11.2741
82 | 2219.2739 | 7.496 | 7.9593 | 11.244
82.1 | 2220.0215 | 7.4761 | 7.9381 | 11.2141
82.2 | 2220.7672 | 7.4561 | 7.9169 | 11.1842
82.3 | 2221.5108 | 7.4363 | 7.8958 | 11.1544
82.4 | 2222.2524 | 7.4165 | 7.8748 | 11.1247
82.5 | 2222.9921 | 7.3967 | 7.8538 | 11.0951
82.6 | 2223.7298 | 7.377 | 7.8329 | 11.0656
82.7 | 2224.4655 | 7.3574 | 7.8121 | 11.0361
82.8 | 2225.1993 | 7.3378 | 7.7913 | 11.0067
82.9 | 2225.9312 | 7.3183 | 7.7705 | 10.9774
83 | 2226.661 | 7.2988 | 7.7498 | 10.9481
83.1 | 2227.389 | 7.2793 | 7.7292 | 10.919
83.2 | 2228.115 | 7.2599 | 7.7086 | 10.8899
83.3 | 2228.839 | 7.2406 | 7.6881 | 10.8609
83.4 | 2229.5611 | 7.2213 | 7.6676 | 10.832
83.5 | 2230.2814 | 7.2021 | 7.6472 | 10.8031
83.6 | 2230.9997 | 7.1829 | 7.6268 | 10.7744
83.7 | 2231.716 | 7.1638 | 7.6065 | 10.7457
83.8 | 2232.4305 | 7.1447 | 7.5862 | 10.7171
83.9 | 2233.1431 | 7.1257 | 7.566 | 10.6885
84 | 2233.8537 | 7.1067 | 7.5459 | 10.6601
84.1 | 2234.5625 | 7.0878 | 7.5258 | 10.6317
84.2 | 2235.2694 | 7.0689 | 7.5057 | 10.6034
84.3 | 2235.9744 | 7.0501 | 7.4858 | 10.5751
84.4 | 2236.6775 | 7.0313 | 7.4658 | 10.547
84.5 | 2237.3788 | 7.0126 | 7.4459 | 10.5189
84.6 | 2238.0782 | 6.9939 | 7.4261 | 10.4909
84.7 | 2238.7757 | 6.9753 | 7.4063 | 10.4629
84.8 | 2239.4714 | 6.9567 | 7.3866 | 10.4351
84.9 | 2240.1652 | 6.9382 | 7.3669 | 10.4073
85 | 2240.8572 | 6.9197 | 7.3473 | 10.3795
85.1 | 2241.5473 | 6.9013 | 7.3278 | 10.3519
85.2 | 2242.2356 | 6.8829 | 7.3082 | 10.3243
85.3 | 2242.9221 | 6.8646 | 7.2888 | 10.2968
85.4 | 2243.6067 | 6.8463 | 7.2694 | 10.2694
85.5 | 2244.2895 | 6.828 | 7.25 | 10.2421
85.6 | 2244.9705 | 6.8099 | 7.2307 | 10.2148
85.7 | 2245.6496 | 6.7917 | 7.2114 | 10.1876
85.8 | 2246.327 | 6.7736 | 7.1922 | 10.1605
85.9 | 2247.0026 | 6.7556 | 7.1731 | 10.1334
86 | 2247.6763 | 6.7376 | 7.154 | 10.1064
86.1 | 2248.3483 | 6.7197 | 7.1349 | 10.0795
86.2 | 2249.0185 | 6.7018 | 7.1159 | 10.0527
86.3 | 2249.6869 | 6.6839 | 7.097 | 10.0259
86.4 | 2250.3535 | 6.6661 | 7.0781 | 9.9992
86.5 | 2251.0183 | 6.6484 | 7.0592 | 9.9726
86.6 | 2251.6814 | 6.6307 | 7.0404 | 9.946
86.7 | 2252.3427 | 6.613 | 7.0217 | 9.9195
86.8 | 2253.0022 | 6.5954 | 7.003 | 9.8931
86.9 | 2253.66 | 6.5778 | 6.9843 | 9.8667
87 | 2254.316 | 6.5603 | 6.9657 | 9.8405
87.1 | 2254.9703 | 6.5428 | 6.9472 | 9.8143
87.2 | 2255.6229 | 6.5254 | 6.9287 | 9.7881
87.3 | 2256.2737 | 6.508 | 6.9102 | 9.7621
87.4 | 2256.9227 | 6.4907 | 6.8918 | 9.7361
87.5 | 2257.5701 | 6.4734 | 6.8735 | 9.7101
87.6 | 2258.2157 | 6.4562 | 6.8552 | 9.6843
87.7 | 2258.8596 | 6.439 | 6.8369 | 9.6585
87.8 | 2259.5018 | 6.4218 | 6.8187 | 9.6328
87.9 | 2260.1423 | 6.4047 | 6.8005 | 9.6071
88 | 2260.781 | 6.3877 | 6.7824 | 9.5815
88.1 | 2261.4181 | 6.3707 | 6.7644 | 9.556
88.2 | 2262.0535 | 6.3537 | 6.7464 | 9.5306
88.3 | 2262.6871 | 6.3368 | 6.7284 | 9.5052
88.4 | 2263.3191 | 6.3199 | 6.7105 | 9.4799
88.5 | 2263.9494 | 6.3031 | 6.6926 | 9.4546
88.6 | 2264.5781 | 6.2863 | 6.6748 | 9.4294
88.7 | 2265.205 | 6.2696 | 6.657 | 9.4043
88.8 | 2265.8303 | 6.2529 | 6.6393 | 9.3793
88.9 | 2266.4539 | 6.2362 | 6.6216 | 9.3543
89 | 2267.0759 | 6.2196 | 6.604 | 9.3294
89.1 | 2267.6962 | 6.203 | 6.5864 | 9.3046
89.2 | 2268.3148 | 6.1865 | 6.5688 | 9.2798
89.3 | 2268.9319 | 6.17 | 6.5513 | 9.2551
89.4 | 2269.5472 | 6.1536 | 6.5339 | 9.2304
89.5 | 2270.1609 | 6.1372 | 6.5165 | 9.2058
89.6 | 2270.773 | 6.1209 | 6.4991 | 9.1813
89.7 | 2271.3835 | 6.1046 | 6.4818 | 9.1569
89.8 | 2271.9923 | 6.0883 | 6.4646 | 9.1325
89.9 | 2272.5995 | 6.0721 | 6.4473 | 9.1082
90 | 2273.2051 | 6.0559 | 6.4302 | 9.0839
90.1 | 2273.8091 | 6.0398 | 6.4131 | 9.0597
90.2 | 2274.4115 | 6.0237 | 6.396 | 9.0356
90.3 | 2275.0122 | 6.0077 | 6.3789 | 9.0115
90.4 | 2275.6114 | 5.9917 | 6.362 | 8.9875
90.5 | 2276.209 | 5.9757 | 6.345 | 8.9636
90.6 | 2276.805 | 5.9598 | 6.3281 | 8.9397
90.7 | 2277.3994 | 5.9439 | 6.3113 | 8.9159
90.8 | 2277.9922 | 5.9281 | 6.2945 | 8.8922
90.9 | 2278.5834 | 5.9123 | 6.2777 | 8.8685
91 | 2279.1731 | 5.8966 | 6.261 | 8.8449
91.1 | 2279.7611 | 5.8809 | 6.2443 | 8.8213
91.2 | 2280.3477 | 5.8652 | 6.2277 | 8.7978
91.3 | 2280.9326 | 5.8496 | 6.2111 | 8.7744
91.4 | 2281.516 | 5.834 | 6.1945 | 8.751
91.5 | 2282.0979 | 5.8185 | 6.178 | 8.7277
91.6 | 2282.6782 | 5.803 | 6.1616 | 8.7045
91.7 | 2283.2569 | 5.7875 | 6.1452 | 8.6813
91.8 | 2283.8341 | 5.7721 | 6.1288 | 8.6582
91.9 | 2284.4098 | 5.7567 | 6.1125 | 8.6351
92 | 2284.9839 | 5.7414 | 6.0962 | 8.6121
92.1 | 2285.5566 | 5.7261 | 6.08 | 8.5892
92.2 | 2286.1276 | 5.7109 | 6.0638 | 8.5663
92.3 | 2286.6972 | 5.6957 | 6.0476 | 8.5435
92.4 | 2287.2653 | 5.6805 | 6.0315 | 8.5207
92.5 | 2287.8318 | 5.6654 | 6.0155 | 8.4981
92.6 | 2288.3968 | 5.6503 | 5.9995 | 8.4754
92.7 | 2288.9604 | 5.6352 | 5.9835 | 8.4529
92.8 | 2289.5224 | 5.6202 | 5.9675 | 8.4303
92.9 | 2290.0829 | 5.6053 | 5.9517 | 8.4079
93 | 2290.6419 | 5.5903 | 5.9358 | 8.3855
93.1 | 2291.1995 | 5.5754 | 5.92 | 8.3632
93.2 | 2291.7555 | 5.5606 | 5.9042 | 8.3409
93.3 | 2292.3101 | 5.5458 | 5.8885 | 8.3187
93.4 | 2292.8632 | 5.531 | 5.8728 | 8.2965
93.5 | 2293.4148 | 5.5163 | 5.8572 | 8.2744
93.6 | 2293.965 | 5.5016 | 5.8416 | 8.2524
93.7 | 2294.5137 | 5.4869 | 5.826 | 8.2304
93.8 | 2295.0609 | 5.4723 | 5.8105 | 8.2085
93.9 | 2295.6067 | 5.4578 | 5.795 | 8.1866
94 | 2296.151 | 5.4432 | 5.7796 | 8.1648
94.1 | 2296.6939 | 5.4287 | 5.7642 | 8.1431
94.2 | 2297.2353 | 5.4143 | 5.7489 | 8.1214
94.3 | 2297.7753 | 5.3999 | 5.7336 | 8.0998
94.4 | 2298.3139 | 5.3855 | 5.7183 | 8.0782
94.5 | 2298.851 | 5.3711 | 5.7031 | 8.0567
94.6 | 2299.3867 | 5.3568 | 5.6879 | 8.0352
94.7 | 2299.9209 | 5.3426 | 5.6727 | 8.0138
94.8 | 2300.4538 | 5.3283 | 5.6576 | 7.9925
94.9 | 2300.9852 | 5.3141 | 5.6425 | 7.9712
95 | 2301.5152 | 5.3 | 5.6275 | 7.95
95.1 | 2302.0438 | 5.2859 | 5.6125 | 7.9288
95.2 | 2302.5709 | 5.2718 | 5.5976 | 7.9077
95.3 | 2303.0967 | 5.2578 | 5.5827 | 7.8866
95.4 | 2303.6211 | 5.2438 | 5.5678 | 7.8656
95.5 | 2304.1441 | 5.2298 | 5.553 | 7.8447
95.6 | 2304.6657 | 5.2159 | 5.5382 | 7.8238
95.7 | 2305.1859 | 5.202 | 5.5234 | 7.803
95.8 | 2305.7047 | 5.1881 | 5.5087 | 7.7822
95.9 | 2306.2221 | 5.1743 | 5.4941 | 7.7615
96 | 2306.7381 | 5.1605 | 5.4794 | 7.7408
96.1 | 2307.2528 | 5.1468 | 5.4648 | 7.7202
96.2 | 2307.7661 | 5.1331 | 5.4503 | 7.6996
96.3 | 2308.2781 | 5.1194 | 5.4358 | 7.6791
96.4 | 2308.7887 | 5.1058 | 5.4213 | 7.6587
96.5 | 2309.2979 | 5.0922 | 5.4069 | 7.6383
96.6 | 2309.8057 | 5.0786 | 5.3925 | 7.6179
96.7 | 2310.3122 | 5.0651 | 5.3781 | 7.5976
96.8 | 2310.8174 | 5.0516 | 5.3638 | 7.5774
96.9 | 2311.3212 | 5.0381 | 5.3495 | 7.5572
97 | 2311.8237 | 5.0247 | 5.3352 | 7.5371
97.1 | 2312.3248 | 5.0114 | 5.321 | 7.517
97.2 | 2312.8246 | 4.998 | 5.3069 | 7.497
97.3 | 2313.3231 | 4.9847 | 5.2927 | 7.477
97.4 | 2313.8202 | 4.9714 | 5.2786 | 7.4571
97.5 | 2314.3161 | 4.9582 | 5.2646 | 7.4373
97.6 | 2314.8106 | 4.945 | 5.2506 | 7.4175
97.7 | 2315.3037 | 4.9318 | 5.2366 | 7.3977
97.8 | 2315.7956 | 4.9187 | 5.2226 | 7.378
97.9 | 2316.2862 | 4.9056 | 5.2087 | 7.3584
98 | 2316.7754 | 4.8925 | 5.1949 | 7.3388
98.1 | 2317.2634 | 4.8795 | 5.181 | 7.3192
98.2 | 2317.75 | 4.8665 | 5.1672 | 7.2997
98.3 | 2318.2354 | 4.8535 | 5.1535 | 7.2803
98.4 | 2318.7194 | 4.8406 | 5.1397 | 7.2609
98.5 | 2319.2022 | 4.8277 | 5.1261 | 7.2416
98.6 | 2319.6837 | 4.8149 | 5.1124 | 7.2223
98.7 | 2320.1639 | 4.802 | 5.0988 | 7.203
98.8 | 2320.6428 | 4.7892 | 5.0852 | 7.1839
98.9 | 2321.1204 | 4.7765 | 5.0717 | 7.1647
99 | 2321.5968 | 4.7638 | 5.0582 | 7.1457
99.1 | 2322.0719 | 4.7511 | 5.0447 | 7.1266
99.2 | 2322.5458 | 4.7384 | 5.0313 | 7.1076
99.3 | 2323.0184 | 4.7258 | 5.0179 | 7.0887
99.4 | 2323.4897 | 4.7132 | 5.0045 | 7.0698
99.5 | 2323.9597 | 4.7007 | 4.9912 | 7.051
99.6 | 2324.4286 | 4.6882 | 4.9779 | 7.0322
99.7 | 2324.8961 | 4.6757 | 4.9646 | 7.0135
99.8 | 2325.3625 | 4.6632 | 4.9514 | 6.9948
99.9 | 2325.8275 | 4.6508 | 4.9382 | 6.9762
100 | 2326.2914 | 4.6384 | 4.9251 | 6.9576
100.1 | 2326.754 | 4.6261 | 4.9119 | 6.9391
100.2 | 2327.2154 | 4.6137 | 4.8989 | 6.9206
100.3 | 2327.6755 | 4.6015 | 4.8858 | 6.9022
100.4 | 2328.1344 | 4.5892 | 4.8728 | 6.8838
100.5 | 2328.5921 | 4.577 | 4.8598 | 6.8655
100.6 | 2329.0486 | 4.5648 | 4.8469 | 6.8472
100.7 | 2329.5039 | 4.5526 | 4.834 | 6.8289
100.8 | 2329.9579 | 4.5405 | 4.8211 | 6.8108
100.9 | 2330.4107 | 4.5284 | 4.8083 | 6.7926
101 | 2330.8624 | 4.5164 | 4.7955 | 6.7745
101.1 | 2331.3128 | 4.5043 | 4.7827 | 6.7565
101.2 | 2331.7621 | 4.4923 | 4.7699 | 6.7385
101.3 | 2332.2101 | 4.4804 | 4.7572 | 6.7206
101.4 | 2332.6569 | 4.4684 | 4.7446 | 6.7027
101.5 | 2333.1026 | 4.4565 | 4.7319 | 6.6848
101.6 | 2333.5471 | 4.4447 | 4.7193 | 6.667
101.7 | 2333.9903 | 4.4328 | 4.7068 | 6.6492
101.8 | 2334.4324 | 4.421 | 4.6942 | 6.6315
101.9 | 2334.8734 | 4.4093 | 4.6817 | 6.6139
102 | 2335.3131 | 4.3975 | 4.6693 | 6.5963
102.1 | 2335.7517 | 4.3858 | 4.6568 | 6.5787
102.2 | 2336.1891 | 4.3741 | 4.6444 | 6.5612
102.3 | 2336.6254 | 4.3625 | 4.6321 | 6.5437
102.4 | 2337.0604 | 4.3509 | 4.6197 | 6.5263
102.5 | 2337.4944 | 4.3393 | 4.6074 | 6.5089
102.6 | 2337.9271 | 4.3277 | 4.5952 | 6.4916
102.7 | 2338.3588 | 4.3162 | 4.5829 | 6.4743
102.8 | 2338.7892 | 4.3047 | 4.5707 | 6.457
102.9 | 2339.2185 | 4.2932 | 4.5585 | 6.4398
103 | 2339.6467 | 4.2818 | 4.5464 | 6.4227
103.1 | 2340.0738 | 4.2704 | 4.5343 | 6.4056
103.2 | 2340.4997 | 4.259 | 4.5222 | 6.3885
103.3 | 2340.9244 | 4.2477 | 4.5102 | 6.3715
103.4 | 2341.3481 | 4.2364 | 4.4982 | 6.3545
103.5 | 2341.7706 | 4.2251 | 4.4862 | 6.3376
103.6 | 2342.192 | 4.2138 | 4.4742 | 6.3207
103.7 | 2342.6122 | 4.2026 | 4.4623 | 6.3039
103.8 | 2343.0314 | 4.1914 | 4.4504 | 6.2871
103.9 | 2343.4494 | 4.1803 | 4.4386 | 6.2704
104 | 2343.8663 | 4.1691 | 4.4268 | 6.2537
104.1 | 2344.2821 | 4.158 | 4.415 | 6.237
104.2 | 2344.6968 | 4.1469 | 4.4032 | 6.2204
104.3 | 2345.1104 | 4.1359 | 4.3915 | 6.2039
104.4 | 2345.5229 | 4.1249 | 4.3798 | 6.1873
104.5 | 2345.9343 | 4.1139 | 4.3681 | 6.1709
104.6 | 2346.3446 | 4.1029 | 4.3565 | 6.1544
104.7 | 2346.7538 | 4.092 | 4.3449 | 6.138
104.8 | 2347.1619 | 4.0811 | 4.3333 | 6.1217
104.9 | 2347.5689 | 4.0703 | 4.3218 | 6.1054
105 | 2347.9748 | 4.0594 | 4.3103 | 6.0891
105.1 | 2348.3797 | 4.0486 | 4.2988 | 6.0729
105.2 | 2348.7835 | 4.0378 | 4.2874 | 6.0567
105.3 | 2349.1862 | 4.0271 | 4.2759 | 6.0406
105.4 | 2349.5878 | 4.0163 | 4.2645 | 6.0245
105.5 | 2349.9884 | 4.0056 | 4.2532 | 6.0085
105.6 | 2350.3879 | 3.995 | 4.2419 | 5.9925
105.7 | 2350.7863 | 3.9843 | 4.2306 | 5.9765
105.8 | 2351.1837 | 3.9737 | 4.2193 | 5.9606
105.9 | 2351.58 | 3.9631 | 4.2081 | 5.9447
106 | 2351.9753 | 3.9526 | 4.1969 | 5.9289
106.1 | 2352.3695 | 3.9421 | 4.1857 | 5.9131
106.2 | 2352.7626 | 3.9316 | 4.1745 | 5.8974
106.3 | 2353.1547 | 3.9211 | 4.1634 | 5.8816
106.4 | 2353.5458 | 3.9107 | 4.1523 | 5.866
106.5 | 2353.9358 | 3.9002 | 4.1413 | 5.8504
106.6 | 2354.3248 | 3.8899 | 4.1302 | 5.8348
106.7 | 2354.7128 | 3.8795 | 4.1192 | 5.8192
106.8 | 2355.0997 | 3.8692 | 4.1083 | 5.8037
106.9 | 2355.4856 | 3.8589 | 4.0973 | 5.7883
107 | 2355.8704 | 3.8486 | 4.0864 | 5.7729
107.1 | 2356.2543 | 3.8383 | 4.0755 | 5.7575
107.2 | 2356.6371 | 3.8281 | 4.0647 | 5.7422
107.3 | 2357.0189 | 3.8179 | 4.0539 | 5.7269
107.4 | 2357.3996 | 3.8078 | 4.0431 | 5.7116
107.5 | 2357.7794 | 3.7976 | 4.0323 | 5.6964
107.6 | 2358.1582 | 3.7875 | 4.0216 | 5.6812
107.7 | 2358.5359 | 3.7774 | 4.0108 | 5.6661
107.8 | 2358.9126 | 3.7674 | 4.0002 | 5.651
107.9 | 2359.2884 | 3.7573 | 3.9895 | 5.636
108 | 2359.6631 | 3.7473 | 3.9789 | 5.621
108.1 | 2360.0368 | 3.7373 | 3.9683 | 5.606
108.2 | 2360.4096 | 3.7274 | 3.9577 | 5.5911
108.3 | 2360.7813 | 3.7175 | 3.9472 | 5.5762
108.4 | 2361.1521 | 3.7076 | 3.9367 | 5.5613
108.5 | 2361.5218 | 3.6977 | 3.9262 | 5.5465
108.6 | 2361.8906 | 3.6878 | 3.9157 | 5.5317
108.7 | 2362.2584 | 3.678 | 3.9053 | 5.517
108.8 | 2362.6252 | 3.6682 | 3.8949 | 5.5023
108.9 | 2362.9911 | 3.6584 | 3.8845 | 5.4877
109 | 2363.356 | 3.6487 | 3.8742 | 5.4731
109.1 | 2363.7199 | 3.639 | 3.8639 | 5.4585
109.2 | 2364.0828 | 3.6293 | 3.8536 | 5.4439
109.3 | 2364.4447 | 3.6196 | 3.8433 | 5.4294
109.4 | 2364.8057 | 3.61 | 3.8331 | 5.415
109.5 | 2365.1658 | 3.6004 | 3.8229 | 5.4006
109.6 | 2365.5249 | 3.5908 | 3.8127 | 5.3862
109.7 | 2365.883 | 3.5812 | 3.8025 | 5.3718
109.8 | 2366.2402 | 3.5717 | 3.7924 | 5.3575
109.9 | 2366.5964 | 3.5622 | 3.7823 | 5.3433
110 | 2366.9516 | 3.5527 | 3.7722 | 5.329
110.1 | 2367.306 | 3.5432 | 3.7622 | 5.3148
110.2 | 2367.6593 | 3.5338 | 3.7522 | 5.3007
110.3 | 2368.0118 | 3.5244 | 3.7422 | 5.2866
110.4 | 2368.3633 | 3.515 | 3.7322 | 5.2725
110.5 | 2368.7138 | 3.5056 | 3.7223 | 5.2585
110.6 | 2369.0635 | 3.4963 | 3.7124 | 5.2445
110.7 | 2369.4122 | 3.487 | 3.7025 | 5.2305
110.8 | 2369.7599 | 3.4777 | 3.6926 | 5.2166
110.9 | 2370.1068 | 3.4684 | 3.6828 | 5.2027
111 | 2370.4527 | 3.4592 | 3.673 | 5.1888
111.1 | 2370.7977 | 3.45 | 3.6632 | 5.175
111.2 | 2371.1418 | 3.4408 | 3.6534 | 5.1612
111.3 | 2371.485 | 3.4316 | 3.6437 | 5.1475
111.4 | 2371.8272 | 3.4225 | 3.634 | 5.1338
111.5 | 2372.1685 | 3.4134 | 3.6243 | 5.1201
111.6 | 2372.509 | 3.4043 | 3.6147 | 5.1064
111.7 | 2372.8485 | 3.3952 | 3.6051 | 5.0928
111.8 | 2373.1871 | 3.3862 | 3.5954 | 5.0793
111.9 | 2373.5248 | 3.3772 | 3.5859 | 5.0658
112 | 2373.8616 | 3.3682 | 3.5763 | 5.0523
112.1 | 2374.1976 | 3.3592 | 3.5668 | 5.0388
112.2 | 2374.5326 | 3.3503 | 3.5573 | 5.0254
112.3 | 2374.8667 | 3.3413 | 3.5478 | 5.012
112.4 | 2375.2 | 3.3324 | 3.5384 | 4.9987
112.5 | 2375.5323 | 3.3236 | 3.529 | 4.9854
112.6 | 2375.8638 | 3.3147 | 3.5196 | 4.9721
112.7 | 2376.1944 | 3.3059 | 3.5102 | 4.9588
112.8 | 2376.5241 | 3.2971 | 3.5008 | 4.9456
112.9 | 2376.8529 | 3.2883 | 3.4915 | 4.9325
113 | 2377.1809 | 3.2795 | 3.4822 | 4.9193
113.1 | 2377.508 | 3.2708 | 3.4729 | 4.9062
113.2 | 2377.8342 | 3.2621 | 3.4637 | 4.8932
113.3 | 2378.1595 | 3.2534 | 3.4545 | 4.8801
113.4 | 2378.484 | 3.2448 | 3.4453 | 4.8671
113.5 | 2378.8076 | 3.2361 | 3.4361 | 4.8542
113.6 | 2379.1304 | 3.2275 | 3.4269 | 4.8412
113.7 | 2379.4522 | 3.2189 | 3.4178 | 4.8283
113.8 | 2379.7733 | 3.2103 | 3.4087 | 4.8155
113.9 | 2380.0935 | 3.2018 | 3.3996 | 4.8027
114 | 2380.4128 | 3.1932 | 3.3906 | 4.7899
114.1 | 2380.7313 | 3.1847 | 3.3816 | 4.7771
114.2 | 2381.0489 | 3.1763 | 3.3725 | 4.7644
114.3 | 2381.3657 | 3.1678 | 3.3636 | 4.7517
114.4 | 2381.6816 | 3.1594 | 3.3546 | 4.7391
114.5 | 2381.9967 | 3.151 | 3.3457 | 4.7264
114.6 | 2382.3109 | 3.1426 | 3.3368 | 4.7138
114.7 | 2382.6244 | 3.1342 | 3.3279 | 4.7013
114.8 | 2382.937 | 3.1258 | 3.319 | 4.6888
114.9 | 2383.2487 | 3.1175 | 3.3102 | 4.6763
115 | 2383.5596 | 3.1092 | 3.3014 | 4.6638
115.1 | 2383.8697 | 3.1009 | 3.2926 | 4.6514
115.2 | 2384.179 | 3.0927 | 3.2838 | 4.639
115.3 | 2384.4874 | 3.0844 | 3.2751 | 4.6267
115.4 | 2384.7951 | 3.0762 | 3.2663 | 4.6143
115.5 | 2385.1019 | 3.068 | 3.2576 | 4.6021
115.6 | 2385.4078 | 3.0599 | 3.249 | 4.5898
115.7 | 2385.713 | 3.0517 | 3.2403 | 4.5776
115.8 | 2386.0174 | 3.0436 | 3.2317 | 4.5654
115.9 | 2386.3209 | 3.0355 | 3.2231 | 4.5532
116 | 2386.6237 | 3.0274 | 3.2145 | 4.5411
116.1 | 2386.9256 | 3.0193 | 3.2059 | 4.529
116.2 | 2387.2267 | 3.0113 | 3.1974 | 4.517
116.3 | 2387.5271 | 3.0033 | 3.1889 | 4.5049
116.4 | 2387.8266 | 2.9953 | 3.1804 | 4.4929
116.5 | 2388.1253 | 2.9873 | 3.1719 | 4.481
116.6 | 2388.4233 | 2.9794 | 3.1635 | 4.469
116.7 | 2388.7204 | 2.9714 | 3.155 | 4.4571
116.8 | 2389.0167 | 2.9635 | 3.1466 | 4.4453
116.9 | 2389.3123 | 2.9556 | 3.1383 | 4.4334
117 | 2389.6071 | 2.9477 | 3.1299 | 4.4216
117.1 | 2389.9011 | 2.9399 | 3.1216 | 4.4098
117.2 | 2390.1943 | 2.9321 | 3.1133 | 4.3981
117.3 | 2390.4867 | 2.9243 | 3.105 | 4.3864
117.4 | 2390.7783 | 2.9165 | 3.0967 | 4.3747
117.5 | 2391.0692 | 2.9087 | 3.0884 | 4.363
117.6 | 2391.3593 | 2.901 | 3.0802 | 4.3514
117.7 | 2391.6486 | 2.8932 | 3.072 | 4.3398
117.8 | 2391.9372 | 2.8855 | 3.0638 | 4.3283
117.9 | 2392.225 | 2.8778 | 3.0557 | 4.3168
118 | 2392.512 | 2.8702 | 3.0475 | 4.3053
118.1 | 2392.7982 | 2.8625 | 3.0394 | 4.2938
118.2 | 2393.0837 | 2.8549 | 3.0313 | 4.2824
118.3 | 2393.3685 | 2.8473 | 3.0233 | 4.271
118.4 | 2393.6524 | 2.8397 | 3.0152 | 4.2596
118.5 | 2393.9356 | 2.8322 | 3.0072 | 4.2482
118.6 | 2394.2181 | 2.8246 | 2.9992 | 4.2369
118.7 | 2394.4998 | 2.8171 | 2.9912 | 4.2256
118.8 | 2394.7808 | 2.8096 | 2.9832 | 4.2144
118.9 | 2395.061 | 2.8021 | 2.9753 | 4.2032
119 | 2395.3405 | 2.7946 | 2.9673 | 4.192
119.1 | 2395.6192 | 2.7872 | 2.9594 | 4.1808
119.2 | 2395.8972 | 2.7798 | 2.9516 | 4.1697
119.3 | 2396.1744 | 2.7724 | 2.9437 | 4.1586
119.4 | 2396.4509 | 2.765 | 2.9359 | 4.1475
119.5 | 2396.7267 | 2.7576 | 2.928 | 4.1364
119.6 | 2397.0017 | 2.7503 | 2.9202 | 4.1254
119.7 | 2397.276 | 2.743 | 2.9125 | 4.1144
119.8 | 2397.5495 | 2.7357 | 2.9047 | 4.1035
119.9 | 2397.8224 | 2.7284 | 2.897 | 4.0926
120 | 2398.0945 | 2.7211 | 2.8893 | 4.0817
120.1 | 2398.3659 | 2.7139 | 2.8816 | 4.0708
120.2 | 2398.6365 | 2.7066 | 2.8739 | 4.0599
120.3 | 2398.9065 | 2.6994 | 2.8662 | 4.0491
120.4 | 2399.1757 | 2.6922 | 2.8586 | 4.0384
120.5 | 2399.4442 | 2.6851 | 2.851 | 4.0276
120.6 | 2399.712 | 2.6779 | 2.8434 | 4.0169
120.7 | 2399.9791 | 2.6708 | 2.8358 | 4.0062
120.8 | 2400.2454 | 2.6637 | 2.8283 | 3.9955
120.9 | 2400.5111 | 2.6566 | 2.8207 | 3.9849
121 | 2400.7761 | 2.6495 | 2.8132 | 3.9743
121.1 | 2401.0403 | 2.6424 | 2.8057 | 3.9637
121.2 | 2401.3038 | 2.6354 | 2.7983 | 3.9531
121.3 | 2401.5667 | 2.6284 | 2.7908 | 3.9426
121.4 | 2401.8288 | 2.6214 | 2.7834 | 3.9321
121.5 | 2402.0903 | 2.6144 | 2.776 | 3.9216
121.6 | 2402.351 | 2.6074 | 2.7686 | 3.9112
121.7 | 2402.6111 | 2.6005 | 2.7612 | 3.9008
121.8 | 2402.8704 | 2.5936 | 2.7539 | 3.8904
121.9 | 2403.1291 | 2.5867 | 2.7465 | 3.88
122 | 2403.3871 | 2.5798 | 2.7392 | 3.8697
122.1 | 2403.6444 | 2.5729 | 2.7319 | 3.8594
122.2 | 2403.901 | 2.5661 | 2.7246 | 3.8491
122.3 | 2404.1569 | 2.5592 | 2.7174 | 3.8388
122.4 | 2404.4121 | 2.5524 | 2.7101 | 3.8286
122.5 | 2404.6667 | 2.5456 | 2.7029 | 3.8184
122.6 | 2404.9206 | 2.5388 | 2.6957 | 3.8083
122.7 | 2405.1738 | 2.5321 | 2.6886 | 3.7981
122.8 | 2405.4263 | 2.5253 | 2.6814 | 3.788
122.9 | 2405.6782 | 2.5186 | 2.6743 | 3.7779
123 | 2405.9294 | 2.5119 | 2.6671 | 3.7678
123.1 | 2406.1799 | 2.5052 | 2.66 | 3.7578
123.2 | 2406.4297 | 2.4985 | 2.6529 | 3.7478
123.3 | 2406.6789 | 2.4919 | 2.6459 | 3.7378
123.4 | 2406.9274 | 2.4852 | 2.6388 | 3.7279
123.5 | 2407.1753 | 2.4786 | 2.6318 | 3.7179
123.6 | 2407.4225 | 2.472 | 2.6248 | 3.708
123.7 | 2407.6691 | 2.4654 | 2.6178 | 3.6982
123.8 | 2407.9149 | 2.4589 | 2.6108 | 3.6883
123.9 | 2408.1602 | 2.4523 | 2.6039 | 3.6785
124 | 2408.4048 | 2.4458 | 2.5969 | 3.6687
124.1 | 2408.6487 | 2.4393 | 2.59 | 3.6589
124.2 | 2408.892 | 2.4328 | 2.5831 | 3.6492
124.3 | 2409.1346 | 2.4263 | 2.5763 | 3.6395
124.4 | 2409.3766 | 2.4198 | 2.5694 | 3.6298
124.5 | 2409.6179 | 2.4134 | 2.5625 | 3.6201
124.6 | 2409.8586 | 2.407 | 2.5557 | 3.6105
124.7 | 2410.0987 | 2.4006 | 2.5489 | 3.6009
124.8 | 2410.3381 | 2.3942 | 2.5421 | 3.5913
124.9 | 2410.5769 | 2.3878 | 2.5354 | 3.5817
125 | 2410.815 | 2.3814 | 2.5286 | 3.5722
125.1 | 2411.0525 | 2.3751 | 2.5219 | 3.5626
125.2 | 2411.2894 | 2.3688 | 2.5152 | 3.5532
125.3 | 2411.5257 | 2.3625 | 2.5085 | 3.5437
125.4 | 2411.7613 | 2.3562 | 2.5018 | 3.5343
125.5 | 2411.9963 | 2.3499 | 2.4951 | 3.5248
125.6 | 2412.2306 | 2.3436 | 2.4885 | 3.5155
125.7 | 2412.4644 | 2.3374 | 2.4818 | 3.5061
125.8 | 2412.6975 | 2.3312 | 2.4752 | 3.4968
125.9 | 2412.93 | 2.325 | 2.4686 | 3.4874
126 | 2413.1619 | 2.3188 | 2.4621 | 3.4782
126.1 | 2413.3931 | 2.3126 | 2.4555 | 3.4689
126.2 | 2413.6238 | 2.3064 | 2.449 | 3.4597
126.3 | 2413.8538 | 2.3003 | 2.4425 | 3.4504
126.4 | 2414.0832 | 2.2942 | 2.4359 | 3.4413
126.5 | 2414.312 | 2.2881 | 2.4295 | 3.4321
126.6 | 2414.5402 | 2.282 | 2.423 | 3.423
126.7 | 2414.7678 | 2.2759 | 2.4165 | 3.4138
126.8 | 2414.9948 | 2.2698 | 2.4101 | 3.4047
126.9 | 2415.2212 | 2.2638 | 2.4037 | 3.3957
127 | 2415.4469 | 2.2578 | 2.3973 | 3.3866
127.1 | 2415.6721 | 2.2517 | 2.3909 | 3.3776
127.2 | 2415.8967 | 2.2457 | 2.3845 | 3.3686
127.3 | 2416.1207 | 2.2398 | 2.3782 | 3.3597
127.4 | 2416.344 | 2.2338 | 2.3718 | 3.3507
127.5 | 2416.5668 | 2.2279 | 2.3655 | 3.3418
127.6 | 2416.789 | 2.2219 | 2.3592 | 3.3329
127.7 | 2417.0106 | 2.216 | 2.3529 | 3.324
127.8 | 2417.2316 | 2.2101 | 2.3467 | 3.3152
127.9 | 2417.452 | 2.2042 | 2.3404 | 3.3063
128 | 2417.6719 | 2.1983 | 2.3342 | 3.2975
128.1 | 2417.8911 | 2.1925 | 2.328 | 3.2887
128.2 | 2418.1098 | 2.1867 | 2.3218 | 3.28
128.3 | 2418.3279 | 2.1808 | 2.3156 | 3.2712
128.4 | 2418.5454 | 2.175 | 2.3094 | 3.2625
128.5 | 2418.7623 | 2.1692 | 2.3033 | 3.2538
128.6 | 2418.9787 | 2.1635 | 2.2971 | 3.2452
128.7 | 2419.1944 | 2.1577 | 2.291 | 3.2365
128.8 | 2419.4096 | 2.1519 | 2.2849 | 3.2279
128.9 | 2419.6242 | 2.1462 | 2.2788 | 3.2193
129 | 2419.8383 | 2.1405 | 2.2728 | 3.2107
129.1 | 2420.0518 | 2.1348 | 2.2667 | 3.2022
129.2 | 2420.2647 | 2.1291 | 2.2607 | 3.1937
129.3 | 2420.477 | 2.1234 | 2.2547 | 3.1852
129.4 | 2420.6888 | 2.1178 | 2.2487 | 3.1767
129.5 | 2420.9 | 2.1121 | 2.2427 | 3.1682
129.6 | 2421.1107 | 2.1065 | 2.2367 | 3.1598
129.7 | 2421.3208 | 2.1009 | 2.2307 | 3.1514
129.8 | 2421.5303 | 2.0953 | 2.2248 | 3.143
129.9 | 2421.7393 | 2.0897 | 2.2189 | 3.1346
130 | 2421.9477 | 2.0842 | 2.213 | 3.1263
130.1 | 2422.1555 | 2.0786 | 2.2071 | 3.1179
130.2 | 2422.3629 | 2.0731 | 2.2012 | 3.1096
130.3 | 2422.5696 | 2.0676 | 2.1953 | 3.1013
130.4 | 2422.7758 | 2.0621 | 2.1895 | 3.0931
130.5 | 2422.9815 | 2.0566 | 2.1837 | 3.0849
130.6 | 2423.1866 | 2.0511 | 2.1778 | 3.0766
130.7 | 2423.3911 | 2.0456 | 2.172 | 3.0684
130.8 | 2423.5952 | 2.0402 | 2.1663 | 3.0603
130.9 | 2423.7986 | 2.0347 | 2.1605 | 3.0521
131 | 2424.0016 | 2.0293 | 2.1547 | 3.044
131.1 | 2424.204 | 2.0239 | 2.149 | 3.0359
131.2 | 2424.4058 | 2.0185 | 2.1433 | 3.0278
131.3 | 2424.6071 | 2.0132 | 2.1376 | 3.0197
131.4 | 2424.8079 | 2.0078 | 2.1319 | 3.0117
131.5 | 2425.0082 | 2.0025 | 2.1262 | 3.0037
131.6 | 2425.2079 | 1.9971 | 2.1205 | 2.9957
131.7 | 2425.407 | 1.9918 | 2.1149 | 2.9877
131.8 | 2425.6057 | 1.9865 | 2.1093 | 2.9797
131.9 | 2425.8038 | 1.9812 | 2.1036 | 2.9718
132 | 2426.0014 | 1.9759 | 2.098 | 2.9639
132.1 | 2426.1985 | 1.9707 | 2.0925 | 2.956
132.2 | 2426.395 | 1.9654 | 2.0869 | 2.9481
132.3 | 2426.591 | 1.9602 | 2.0813 | 2.9403
132.4 | 2426.7865 | 1.955 | 2.0758 | 2.9324
132.5 | 2426.9815 | 1.9498 | 2.0702 | 2.9246
132.6 | 2427.176 | 1.9446 | 2.0647 | 2.9168
132.7 | 2427.3699 | 1.9394 | 2.0592 | 2.9091
132.8 | 2427.5633 | 1.9342 | 2.0538 | 2.9013
132.9 | 2427.7562 | 1.9291 | 2.0483 | 2.8936
133 | 2427.9486 | 1.9239 | 2.0428 | 2.8859
133.1 | 2428.1405 | 1.9188 | 2.0374 | 2.8782
133.2 | 2428.3319 | 1.9137 | 2.032 | 2.8706
133.3 | 2428.5227 | 1.9086 | 2.0266 | 2.8629
133.4 | 2428.7131 | 1.9035 | 2.0212 | 2.8553
133.5 | 2428.9029 | 1.8985 | 2.0158 | 2.8477
133.6 | 2429.0923 | 1.8934 | 2.0104 | 2.8401
133.7 | 2429.2811 | 1.8884 | 2.0051 | 2.8325
133.8 | 2429.4694 | 1.8833 | 1.9997 | 2.825
133.9 | 2429.6573 | 1.8783 | 1.9944 | 2.8175
134 | 2429.8446 | 1.8733 | 1.9891 | 2.81
134.1 | 2430.0314 | 1.8683 | 1.9838 | 2.8025
134.2 | 2430.2178 | 1.8633 | 1.9785 | 2.795
134.3 | 2430.4036 | 1.8584 | 1.9732 | 2.7876
134.4 | 2430.589 | 1.8534 | 1.968 | 2.7801
134.5 | 2430.7738 | 1.8485 | 1.9627 | 2.7727
134.6 | 2430.9582 | 1.8436 | 1.9575 | 2.7654
134.7 | 2431.142 | 1.8387 | 1.9523 | 2.758
134.8 | 2431.3254 | 1.8338 | 1.9471 | 2.7506
134.9 | 2431.5083 | 1.8289 | 1.9419 | 2.7433
135 | 2431.6907 | 1.824 | 1.9367 | 2.736
135.1 | 2431.8726 | 1.8192 | 1.9316 | 2.7287
135.2 | 2432.054 | 1.8143 | 1.9264 | 2.7215
135.3 | 2432.235 | 1.8095 | 1.9213 | 2.7142
135.4 | 2432.4155 | 1.8047 | 1.9162 | 2.707
135.5 | 2432.5954 | 1.7999 | 1.9111 | 2.6998
135.6 | 2432.7749 | 1.7951 | 1.906 | 2.6926
135.7 | 2432.954 | 1.7903 | 1.9009 | 2.6854
135.8 | 2433.1325 | 1.7855 | 1.8959 | 2.6783
135.9 | 2433.3106 | 1.7808 | 1.8908 | 2.6711
136 | 2433.4882 | 1.776 | 1.8858 | 2.664
136.1 | 2433.6653 | 1.7713 | 1.8807 | 2.6569
136.2 | 2433.842 | 1.7666 | 1.8757 | 2.6499
136.3 | 2434.0182 | 1.7619 | 1.8707 | 2.6428
136.4 | 2434.1939 | 1.7572 | 1.8658 | 2.6358
136.5 | 2434.3691 | 1.7525 | 1.8608 | 2.6287
136.6 | 2434.5439 | 1.7478 | 1.8558 | 2.6217
136.7 | 2434.7182 | 1.7432 | 1.8509 | 2.6148
136.8 | 2434.8921 | 1.7385 | 1.846 | 2.6078
136.9 | 2435.0655 | 1.7339 | 1.841 | 2.6008
137 | 2435.2384 | 1.7293 | 1.8361 | 2.5939
137.1 | 2435.4109 | 1.7247 | 1.8313 | 2.587
137.2 | 2435.5829 | 1.7201 | 1.8264 | 2.5801
137.3 | 2435.7544 | 1.7155 | 1.8215 | 2.5733
137.4 | 2435.9255 | 1.7109 | 1.8167 | 2.5664
137.5 | 2436.0962 | 1.7064 | 1.8118 | 2.5596
137.6 | 2436.2664 | 1.7018 | 1.807 | 2.5527
137.7 | 2436.4361 | 1.6973 | 1.8022 | 2.5459
137.8 | 2436.6054 | 1.6928 | 1.7974 | 2.5392
137.9 | 2436.7742 | 1.6883 | 1.7926 | 2.5324
138 | 2436.9426 | 1.6838 | 1.7878 | 2.5257
138.1 | 2437.1105 | 1.6793 | 1.7831 | 2.5189
138.2 | 2437.278 | 1.6748 | 1.7783 | 2.5122
138.3 | 2437.445 | 1.6704 | 1.7736 | 2.5055
138.4 | 2437.6116 | 1.6659 | 1.7689 | 2.4989
138.5 | 2437.7777 | 1.6615 | 1.7642 | 2.4922
138.6 | 2437.9435 | 1.657 | 1.7595 | 2.4856
138.7 | 2438.1087 | 1.6526 | 1.7548 | 2.479
138.8 | 2438.2735 | 1.6482 | 1.7501 | 2.4724
138.9 | 2438.4379 | 1.6438 | 1.7454 | 2.4658
139 | 2438.6019 | 1.6395 | 1.7408 | 2.4592
139.1 | 2438.7654 | 1.6351 | 1.7361 | 2.4527
139.2 | 2438.9285 | 1.6307 | 1.7315 | 2.4461
139.3 | 2439.0911 | 1.6264 | 1.7269 | 2.4396
139.4 | 2439.2533 | 1.6221 | 1.7223 | 2.4331
139.5 | 2439.4151 | 1.6178 | 1.7177 | 2.4266
139.6 | 2439.5764 | 1.6134 | 1.7132 | 2.4202
139.7 | 2439.7373 | 1.6091 | 1.7086 | 2.4137
139.8 | 2439.8978 | 1.6049 | 1.704 | 2.4073
139.9 | 2440.0579 | 1.6006 | 1.6995 | 2.4009
140 | 2440.2175 | 1.5963 | 1.695 | 2.3945
140.1 | 2440.3767 | 1.5921 | 1.6905 | 2.3881
140.2 | 2440.5355 | 1.5878 | 1.686 | 2.3818
140.3 | 2440.6939 | 1.5836 | 1.6815 | 2.3754
140.4 | 2440.8518 | 1.5794 | 1.677 | 2.3691
140.5 | 2441.0093 | 1.5752 | 1.6725 | 2.3628
140.6 | 2441.1664 | 1.571 | 1.6681 | 2.3565
140.7 | 2441.3231 | 1.5668 | 1.6636 | 2.3502
140.8 | 2441.4794 | 1.5626 | 1.6592 | 2.3439
140.9 | 2441.6352 | 1.5585 | 1.6548 | 2.3377
141 | 2441.7906 | 1.5543 | 1.6504 | 2.3315
141.1 | 2441.9457 | 1.5502 | 1.646 | 2.3253
141.2 | 2442.1003 | 1.5461 | 1.6416 | 2.3191
141.3 | 2442.2545 | 1.5419 | 1.6372 | 2.3129
141.4 | 2442.4082 | 1.5378 | 1.6329 | 2.3067
141.5 | 2442.5616 | 1.5337 | 1.6285 | 2.3006
141.6 | 2442.7146 | 1.5296 | 1.6242 | 2.2945
141.7 | 2442.8671 | 1.5256 | 1.6199 | 2.2884
141.8 | 2443.0193 | 1.5215 | 1.6155 | 2.2823
141.9 | 2443.171 | 1.5175 | 1.6112 | 2.2762
142 | 2443.3224 | 1.5134 | 1.6069 | 2.2701
142.1 | 2443.4733 | 1.5094 | 1.6027 | 2.2641
142.2 | 2443.6239 | 1.5054 | 1.5984 | 2.2581
142.3 | 2443.774 | 1.5014 | 1.5941 | 2.252
142.4 | 2443.9237 | 1.4974 | 1.5899 | 2.246
142.5 | 2444.0731 | 1.4934 | 1.5857 | 2.2401
142.6 | 2444.222 | 1.4894 | 1.5814 | 2.2341
142.7 | 2444.3706 | 1.4854 | 1.5772 | 2.2281
142.8 | 2444.5187 | 1.4815 | 1.573 | 2.2222
142.9 | 2444.6665 | 1.4775 | 1.5688 | 2.2163
143 | 2444.8138 | 1.4736 | 1.5647 | 2.2104
143.1 | 2444.9608 | 1.4697 | 1.5605 | 2.2045
143.2 | 2445.1074 | 1.4658 | 1.5563 | 2.1986
143.3 | 2445.2535 | 1.4619 | 1.5522 | 2.1928
143.4 | 2445.3993 | 1.458 | 1.5481 | 2.1869
143.5 | 2445.5447 | 1.4541 | 1.5439 | 2.1811
143.6 | 2445.6898 | 1.4502 | 1.5398 | 2.1753
143.7 | 2445.8344 | 1.4463 | 1.5357 | 2.1695
143.8 | 2445.9786 | 1.4425 | 1.5316 | 2.1637
143.9 | 2446.1225 | 1.4387 | 1.5276 | 2.158
144 | 2446.266 | 1.4348 | 1.5235 | 2.1522
144.1 | 2446.4091 | 1.431 | 1.5194 | 2.1465
144.2 | 2446.5518 | 1.4272 | 1.5154 | 2.1408
144.3 | 2446.6942 | 1.4234 | 1.5113 | 2.1351
144.4 | 2446.8361 | 1.4196 | 1.5073 | 2.1294
144.5 | 2446.9777 | 1.4158 | 1.5033 | 2.1237
144.6 | 2447.1189 | 1.412 | 1.4993 | 2.1181
144.7 | 2447.2597 | 1.4083 | 1.4953 | 2.1124
144.8 | 2447.4002 | 1.4045 | 1.4913 | 2.1068
144.9 | 2447.5403 | 1.4008 | 1.4874 | 2.1012
145 | 2447.68 | 1.3971 | 1.4834 | 2.0956
145.1 | 2447.8193 | 1.3933 | 1.4794 | 2.09
145.2 | 2447.9583 | 1.3896 | 1.4755 | 2.0844
145.3 | 2448.0969 | 1.3859 | 1.4716 | 2.0789
145.4 | 2448.2351 | 1.3822 | 1.4677 | 2.0734
145.5 | 2448.3729 | 1.3786 | 1.4638 | 2.0678
145.6 | 2448.5104 | 1.3749 | 1.4599 | 2.0623
145.7 | 2448.6475 | 1.3712 | 1.456 | 2.0568
145.8 | 2448.7843 | 1.3676 | 1.4521 | 2.0514
145.9 | 2448.9207 | 1.3639 | 1.4482 | 2.0459
146 | 2449.0567 | 1.3603 | 1.4444 | 2.0405
146.1 | 2449.1924 | 1.3567 | 1.4405 | 2.035
146.2 | 2449.3277 | 1.3531 | 1.4367 | 2.0296
146.3 | 2449.4626 | 1.3495 | 1.4329 | 2.0242
146.4 | 2449.5972 | 1.3459 | 1.429 | 2.0188
146.5 | 2449.7315 | 1.3423 | 1.4252 | 2.0134
146.6 | 2449.8653 | 1.3387 | 1.4214 | 2.0081
146.7 | 2449.9988 | 1.3351 | 1.4177 | 2.0027
146.8 | 2450.132 | 1.3316 | 1.4139 | 1.9974
146.9 | 2450.2648 | 1.328 | 1.4101 | 1.9921
147 | 2450.3973 | 1.3245 | 1.4064 | 1.9868
147.1 | 2450.5294 | 1.321 | 1.4026 | 1.9815
147.2 | 2450.6611 | 1.3175 | 1.3989 | 1.9762
147.3 | 2450.7925 | 1.314 | 1.3952 | 1.9709
147.4 | 2450.9235 | 1.3105 | 1.3914 | 1.9657
147.5 | 2451.0542 | 1.307 | 1.3877 | 1.9604
147.6 | 2451.1846 | 1.3035 | 1.384 | 1.9552
147.7 | 2451.3146 | 1.3 | 1.3803 | 1.95
147.8 | 2451.4442 | 1.2965 | 1.3767 | 1.9448
147.9 | 2451.5736 | 1.2931 | 1.373 | 1.9396
148 | 2451.7025 | 1.2897 | 1.3693 | 1.9345
148.1 | 2451.8311 | 1.2862 | 1.3657 | 1.9293
148.2 | 2451.9594 | 1.2828 | 1.3621 | 1.9242
148.3 | 2452.0874 | 1.2794 | 1.3584 | 1.9191
148.4 | 2452.215 | 1.276 | 1.3548 | 1.914
148.5 | 2452.3422 | 1.2726 | 1.3512 | 1.9089
148.6 | 2452.4691 | 1.2692 | 1.3476 | 1.9038
148.7 | 2452.5957 | 1.2658 | 1.344 | 1.8987
148.8 | 2452.722 | 1.2624 | 1.3404 | 1.8936
148.9 | 2452.8479 | 1.2591 | 1.3369 | 1.8886
149 | 2452.9734 | 1.2557 | 1.3333 | 1.8836
149.1 | 2453.0987 | 1.2524 | 1.3298 | 1.8786
149.2 | 2453.2236 | 1.249 | 1.3262 | 1.8736
149.3 | 2453.3481 | 1.2457 | 1.3227 | 1.8686
149.4 | 2453.4724 | 1.2424 | 1.3192 | 1.8636
149.5 | 2453.5963 | 1.2391 | 1.3157 | 1.8586
149.6 | 2453.7199 | 1.2358 | 1.3122 | 1.8537
149.7 | 2453.8431 | 1.2325 | 1.3087 | 1.8487
149.8 | 2453.966 | 1.2292 | 1.3052 | 1.8438
149.9 | 2454.0886 | 1.2259 | 1.3017 | 1.8389
150 | 2454.2109 | 1.2227 | 1.2982 | 1.834
150.1 | 2454.3328 | 1.2194 | 1.2948 | 1.8291
150.2 | 2454.4545 | 1.2162 | 1.2913 | 1.8243
150.3 | 2454.5758 | 1.2129 | 1.2879 | 1.8194
150.4 | 2454.6967 | 1.2097 | 1.2845 | 1.8145
150.5 | 2454.8174 | 1.2065 | 1.281 | 1.8097
150.6 | 2454.9377 | 1.2033 | 1.2776 | 1.8049
150.7 | 2455.0577 | 1.2001 | 1.2742 | 1.8001
150.8 | 2455.1774 | 1.1969 | 1.2708 | 1.7953
150.9 | 2455.2968 | 1.1937 | 1.2674 | 1.7905
151 | 2455.4158 | 1.1905 | 1.2641 | 1.7857
151.1 | 2455.5345 | 1.1873 | 1.2607 | 1.781
151.2 | 2455.653 | 1.1842 | 1.2573 | 1.7762
151.3 | 2455.7711 | 1.181 | 1.254 | 1.7715
151.4 | 2455.8888 | 1.1779 | 1.2507 | 1.7668
151.5 | 2456.0063 | 1.1747 | 1.2473 | 1.7621
151.6 | 2456.1235 | 1.1716 | 1.244 | 1.7574
151.7 | 2456.2403 | 1.1685 | 1.2407 | 1.7527
151.8 | 2456.3569 | 1.1654 | 1.2374 | 1.7481
151.9 | 2456.4731 | 1.1623 | 1.2341 | 1.7434
152 | 2456.589 | 1.1592 | 1.2308 | 1.7388
152.1 | 2456.7046 | 1.1561 | 1.2275 | 1.7341
152.2 | 2456.8199 | 1.153 | 1.2243 | 1.7295
152.3 | 2456.9349 | 1.1499 | 1.221 | 1.7249
152.4 | 2457.0496 | 1.1469 | 1.2177 | 1.7203
152.5 | 2457.164 | 1.1438 | 1.2145 | 1.7157
152.6 | 2457.2781 | 1.1408 | 1.2113 | 1.7112
152.7 | 2457.3918 | 1.1377 | 1.208 | 1.7066
152.8 | 2457.5053 | 1.1347 | 1.2048 | 1.7021
152.9 | 2457.6185 | 1.1317 | 1.2016 | 1.6975
153 | 2457.7313 | 1.1287 | 1.1984 | 1.693
153.1 | 2457.8439 | 1.1257 | 1.1952 | 1.6885
153.2 | 2457.9562 | 1.1227 | 1.192 | 1.684
153.3 | 2458.0681 | 1.1197 | 1.1889 | 1.6795
153.4 | 2458.1798 | 1.1167 | 1.1857 | 1.675
153.5 | 2458.2912 | 1.1137 | 1.1825 | 1.6706
153.6 | 2458.4023 | 1.1108 | 1.1794 | 1.6661
153.7 | 2458.513 | 1.1078 | 1.1763 | 1.6617
153.8 | 2458.6235 | 1.1048 | 1.1731 | 1.6573
153.9 | 2458.7337 | 1.1019 | 1.17 | 1.6529
154 | 2458.8436 | 1.099 | 1.1669 | 1.6485
154.1 | 2458.9532 | 1.096 | 1.1638 | 1.6441
154.2 | 2459.0625 | 1.0931 | 1.1607 | 1.6397
154.3 | 2459.1715 | 1.0902 | 1.1576 | 1.6353
154.4 | 2459.2803 | 1.0873 | 1.1545 | 1.631
154.5 | 2459.3887 | 1.0844 | 1.1514 | 1.6266
154.6 | 2459.4969 | 1.0815 | 1.1484 | 1.6223
154.7 | 2459.6047 | 1.0786 | 1.1453 | 1.618
154.8 | 2459.7123 | 1.0758 | 1.1423 | 1.6137
154.9 | 2459.8196 | 1.0729 | 1.1392 | 1.6094
155 | 2459.9266 | 1.07 | 1.1362 | 1.6051
155.1 | 2460.0333 | 1.0672 | 1.1332 | 1.6008
155.2 | 2460.1398 | 1.0644 | 1.1301 | 1.5965
155.3 | 2460.2459 | 1.0615 | 1.1271 | 1.5923
155.4 | 2460.3518 | 1.0587 | 1.1241 | 1.588
155.5 | 2460.4574 | 1.0559 | 1.1211 | 1.5838
155.6 | 2460.5627 | 1.0531 | 1.1181 | 1.5796
155.7 | 2460.6677 | 1.0503 | 1.1152 | 1.5754
155.8 | 2460.7724 | 1.0475 | 1.1122 | 1.5712
155.9 | 2460.8769 | 1.0447 | 1.1092 | 1.567
156 | 2460.9811 | 1.0419 | 1.1063 | 1.5628
156.1 | 2461.085 | 1.0391 | 1.1033 | 1.5587
156.2 | 2461.1887 | 1.0364 | 1.1004 | 1.5545
156.3 | 2461.292 | 1.0336 | 1.0975 | 1.5504
156.4 | 2461.3951 | 1.0308 | 1.0945 | 1.5463
156.5 | 2461.4979 | 1.0281 | 1.0916 | 1.5421
156.6 | 2461.6004 | 1.0254 | 1.0887 | 1.538
156.7 | 2461.7027 | 1.0226 | 1.0858 | 1.5339
156.8 | 2461.8047 | 1.0199 | 1.0829 | 1.5299
156.9 | 2461.9064 | 1.0172 | 1.08 | 1.5258
157 | 2462.0079 | 1.0145 | 1.0772 | 1.5217
157.1 | 2462.109 | 1.0118 | 1.0743 | 1.5177
157.2 | 2462.2099 | 1.0091 | 1.0714 | 1.5136
157.3 | 2462.3106 | 1.0064 | 1.0686 | 1.5096
157.4 | 2462.411 | 1.0037 | 1.0657 | 1.5056
157.5 | 2462.5111 | 1.001 | 1.0629 | 1.5016
157.6 | 2462.6109 | 0.99837 | 1.0601 | 1.4976
157.7 | 2462.7105 | 0.99571 | 1.0572 | 1.4936
157.8 | 2462.8098 | 0.99306 | 1.0544 | 1.4896
157.9 | 2462.9088 | 0.99042 | 1.0516 | 1.4856
158 | 2463.0076 | 0.98778 | 1.0488 | 1.4817
158.1 | 2463.1061 | 0.98515 | 1.046 | 1.4777
158.2 | 2463.2044 | 0.98253 | 1.0432 | 1.4738
158.3 | 2463.3024 | 0.97991 | 1.0405 | 1.4699
158.4 | 2463.4001 | 0.9773 | 1.0377 | 1.466
158.5 | 2463.4976 | 0.9747 | 1.0349 | 1.462
158.6 | 2463.5948 | 0.9721 | 1.0322 | 1.4582
158.7 | 2463.6917 | 0.96951 | 1.0294 | 1.4543
158.8 | 2463.7884 | 0.96693 | 1.0267 | 1.4504
158.9 | 2463.8848 | 0.96436 | 1.024 | 1.4465
159 | 2463.981 | 0.96179 | 1.0212 | 1.4427
159.1 | 2464.0769 | 0.95923 | 1.0185 | 1.4388
159.2 | 2464.1726 | 0.95667 | 1.0158 | 1.435
159.3 | 2464.268 | 0.95412 | 1.0131 | 1.4312
159.4 | 2464.3632 | 0.95158 | 1.0104 | 1.4274
159.5 | 2464.4581 | 0.94905 | 1.0077 | 1.4236
159.6 | 2464.5527 | 0.94652 | 1.005 | 1.4198
159.7 | 2464.6471 | 0.944 | 1.0023 | 1.416
159.8 | 2464.7413 | 0.94149 | 0.99967 | 1.4122
159.9 | 2464.8352 | 0.93898 | 0.99701 | 1.4085
160 | 2464.9288 | 0.93648 | 0.99435 | 1.4047
160.1 | 2465.0222 | 0.93399 | 0.9917 | 1.401
160.2 | 2465.1154 | 0.9315 | 0.98906 | 1.3972
160.3 | 2465.2083 | 0.92902 | 0.98643 | 1.3935
160.4 | 2465.3009 | 0.92654 | 0.9838 | 1.3898
160.5 | 2465.3933 | 0.92408 | 0.98118 | 1.3861
160.6 | 2465.4855 | 0.92161 | 0.97857 | 1.3824
160.7 | 2465.5774 | 0.91916 | 0.97596 | 1.3787
160.8 | 2465.6691 | 0.91671 | 0.97336 | 1.3751
160.9 | 2465.7605 | 0.91427 | 0.97077 | 1.3714
161 | 2465.8517 | 0.91184 | 0.96819 | 1.3678
161.1 | 2465.9426 | 0.90941 | 0.96561 | 1.3641
161.2 | 2466.0333 | 0.90699 | 0.96304 | 1.3605
161.3 | 2466.1238 | 0.90457 | 0.96047 | 1.3569
161.4 | 2466.214 | 0.90216 | 0.95791 | 1.3532
161.5 | 2466.304 | 0.89976 | 0.95536 | 1.3496
161.6 | 2466.3937 | 0.89736 | 0.95282 | 1.346
161.7 | 2466.4832 | 0.89497 | 0.95028 | 1.3425
161.8 | 2466.5725 | 0.89259 | 0.94775 | 1.3389
161.9 | 2466.6615 | 0.89021 | 0.94523 | 1.3353
162 | 2466.7503 | 0.88784 | 0.94271 | 1.3318
162.1 | 2466.8388 | 0.88548 | 0.9402 | 1.3282
162.2 | 2466.9272 | 0.88312 | 0.93769 | 1.3247
162.3 | 2467.0152 | 0.88077 | 0.9352 | 1.3212
162.4 | 2467.1031 | 0.87842 | 0.93271 | 1.3176
162.5 | 2467.1907 | 0.87608 | 0.93022 | 1.3141
162.6 | 2467.2781 | 0.87375 | 0.92775 | 1.3106
162.7 | 2467.3652 | 0.87142 | 0.92527 | 1.3071
162.8 | 2467.4521 | 0.8691 | 0.92281 | 1.3037
162.9 | 2467.5388 | 0.86679 | 0.92035 | 1.3002
163 | 2467.6252 | 0.86448 | 0.9179 | 1.2967
163.1 | 2467.7115 | 0.86218 | 0.91546 | 1.2933
163.2 | 2467.7974 | 0.85988 | 0.91302 | 1.2898
163.3 | 2467.8832 | 0.85759 | 0.91059 | 1.2864
163.4 | 2467.9687 | 0.85531 | 0.90816 | 1.283
163.5 | 2468.054 | 0.85303 | 0.90574 | 1.2795
163.6 | 2468.1391 | 0.85076 | 0.90333 | 1.2761
163.7 | 2468.224 | 0.84849 | 0.90093 | 1.2727
163.8 | 2468.3086 | 0.84623 | 0.89853 | 1.2693
163.9 | 2468.393 | 0.84398 | 0.89613 | 1.266
164 | 2468.4772 | 0.84173 | 0.89375 | 1.2626
164.1 | 2468.5611 | 0.83949 | 0.89137 | 1.2592
164.2 | 2468.6448 | 0.83725 | 0.88899 | 1.2559
164.3 | 2468.7283 | 0.83502 | 0.88663 | 1.2525
164.4 | 2468.8116 | 0.8328 | 0.88427 | 1.2492
164.5 | 2468.8947 | 0.83058 | 0.88191 | 1.2459
164.6 | 2468.9775 | 0.82837 | 0.87956 | 1.2426
164.7 | 2469.0601 | 0.82616 | 0.87722 | 1.2392
164.8 | 2469.1425 | 0.82396 | 0.87488 | 1.2359
164.9 | 2469.2247 | 0.82177 | 0.87255 | 1.2327
165 | 2469.3067 | 0.81958 | 0.87023 | 1.2294
165.1 | 2469.3884 | 0.8174 | 0.86791 | 1.2261
165.2 | 2469.4699 | 0.81522 | 0.8656 | 1.2228
165.3 | 2469.5512 | 0.81305 | 0.8633 | 1.2196
165.4 | 2469.6323 | 0.81089 | 0.861 | 1.2163
165.5 | 2469.7132 | 0.80873 | 0.8587 | 1.2131
165.6 | 2469.7938 | 0.80657 | 0.85642 | 1.2099
165.7 | 2469.8743 | 0.80442 | 0.85414 | 1.2066
165.8 | 2469.9545 | 0.80228 | 0.85186 | 1.2034
165.9 | 2470.0345 | 0.80015 | 0.84959 | 1.2002
166 | 2470.1143 | 0.79801 | 0.84733 | 1.197
166.1 | 2470.1939 | 0.79589 | 0.84507 | 1.1938
166.2 | 2470.2733 | 0.79377 | 0.84282 | 1.1907
166.3 | 2470.3525 | 0.79166 | 0.84058 | 1.1875
166.4 | 2470.4314 | 0.78955 | 0.83834 | 1.1843
166.5 | 2470.5102 | 0.78745 | 0.83611 | 1.1812
166.6 | 2470.5887 | 0.78535 | 0.83388 | 1.178
166.7 | 2470.667 | 0.78326 | 0.83166 | 1.1749
166.8 | 2470.7451 | 0.78117 | 0.82945 | 1.1718
166.9 | 2470.823 | 0.77909 | 0.82724 | 1.1686
167 | 2470.9007 | 0.77702 | 0.82503 | 1.1655
167.1 | 2470.9782 | 0.77495 | 0.82284 | 1.1624
167.2 | 2471.0555 | 0.77288 | 0.82065 | 1.1593
167.3 | 2471.1326 | 0.77082 | 0.81846 | 1.1562
167.4 | 2471.2095 | 0.76877 | 0.81628 | 1.1532
167.5 | 2471.2862 | 0.76672 | 0.81411 | 1.1501
167.6 | 2471.3626 | 0.76468 | 0.81194 | 1.147
167.7 | 2471.4389 | 0.76265 | 0.80978 | 1.144
167.8 | 2471.515 | 0.76062 | 0.80762 | 1.1409
167.9 | 2471.5908 | 0.75859 | 0.80547 | 1.1379
168 | 2471.6665 | 0.75657 | 0.80332 | 1.1349
168.1 | 2471.7419 | 0.75455 | 0.80118 | 1.1318
168.2 | 2471.8172 | 0.75254 | 0.79905 | 1.1288
168.3 | 2471.8922 | 0.75054 | 0.79692 | 1.1258
168.4 | 2471.9671 | 0.74854 | 0.7948 | 1.1228
168.5 | 2472.0417 | 0.74655 | 0.79268 | 1.1198
168.6 | 2472.1162 | 0.74456 | 0.79057 | 1.1168
168.7 | 2472.1905 | 0.74258 | 0.78847 | 1.1139
168.8 | 2472.2645 | 0.7406 | 0.78637 | 1.1109
168.9 | 2472.3384 | 0.73863 | 0.78427 | 1.1079
169 | 2472.412 | 0.73666 | 0.78218 | 1.105
169.1 | 2472.4855 | 0.7347 | 0.7801 | 1.102
169.2 | 2472.5588 | 0.73274 | 0.77802 | 1.0991
169.3 | 2472.6319 | 0.73079 | 0.77595 | 1.0962
169.4 | 2472.7048 | 0.72884 | 0.77389 | 1.0933
169.5 | 2472.7774 | 0.7269 | 0.77182 | 1.0904
169.6 | 2472.8499 | 0.72497 | 0.76977 | 1.0875
169.7 | 2472.9222 | 0.72304 | 0.76772 | 1.0846
169.8 | 2472.9944 | 0.72111 | 0.76567 | 1.0817
169.9 | 2473.0663 | 0.71919 | 0.76364 | 1.0788
170 | 2473.138 | 0.71728 | 0.7616 | 1.0759
170.1 | 2473.2095 | 0.71537 | 0.75957 | 1.073
170.2 | 2473.2809 | 0.71346 | 0.75755 | 1.0702
170.3 | 2473.352 | 0.71156 | 0.75553 | 1.0673
170.4 | 2473.423 | 0.70967 | 0.75352 | 1.0645
170.5 | 2473.4938 | 0.70778 | 0.75151 | 1.0617
170.6 | 2473.5644 | 0.70589 | 0.74951 | 1.0588
170.7 | 2473.6348 | 0.70401 | 0.74752 | 1.056
170.8 | 2473.705 | 0.70214 | 0.74553 | 1.0532
170.9 | 2473.775 | 0.70027 | 0.74354 | 1.0504
171 | 2473.8449 | 0.6984 | 0.74156 | 1.0476
171.1 | 2473.9145 | 0.69654 | 0.73959 | 1.0448
171.2 | 2473.984 | 0.69469 | 0.73762 | 1.042
171.3 | 2474.0533 | 0.69284 | 0.73565 | 1.0393
171.4 | 2474.1224 | 0.69099 | 0.73369 | 1.0365
171.5 | 2474.1913 | 0.68915 | 0.73174 | 1.0337
171.6 | 2474.26 | 0.68732 | 0.72979 | 1.031
171.7 | 2474.3286 | 0.68549 | 0.72785 | 1.0282
171.8 | 2474.3969 | 0.68366 | 0.72591 | 1.0255
171.9 | 2474.4651 | 0.68184 | 0.72398 | 1.0228
172 | 2474.5331 | 0.68002 | 0.72205 | 1.02
172.1 | 2474.6009 | 0.67821 | 0.72012 | 1.0173
172.2 | 2474.6686 | 0.67641 | 0.71821 | 1.0146
172.3 | 2474.736 | 0.6746 | 0.71629 | 1.0119
172.4 | 2474.8033 | 0.67281 | 0.71439 | 1.0092
172.5 | 2474.8704 | 0.67102 | 0.71248 | 1.0065
172.6 | 2474.9373 | 0.66923 | 0.71059 | 1.0038
172.7 | 2475.0041 | 0.66745 | 0.70869 | 1.0012
172.8 | 2475.0706 | 0.66567 | 0.70681 | 0.9985
172.9 | 2475.137 | 0.6639 | 0.70492 | 0.99585
173 | 2475.2032 | 0.66213 | 0.70305 | 0.99319
173.1 | 2475.2693 | 0.66037 | 0.70118 | 0.99055
173.2 | 2475.3351 | 0.65861 | 0.69931 | 0.98791
173.3 | 2475.4008 | 0.65685 | 0.69745 | 0.98528
173.4 | 2475.4663 | 0.6551 | 0.69559 | 0.98266
173.5 | 2475.5317 | 0.65336 | 0.69374 | 0.98004
173.6 | 2475.5968 | 0.65162 | 0.69189 | 0.97743
173.7 | 2475.6618 | 0.64988 | 0.69005 | 0.97483
173.8 | 2475.7266 | 0.64815 | 0.68821 | 0.97223
173.9 | 2475.7913 | 0.64643 | 0.68638 | 0.96964
174 | 2475.8558 | 0.64471 | 0.68455 | 0.96706
174.1 | 2475.9201 | 0.64299 | 0.68272 | 0.96448
174.2 | 2475.9842 | 0.64128 | 0.68091 | 0.96191
174.3 | 2476.0481 | 0.63957 | 0.67909 | 0.95935
174.4 | 2476.1119 | 0.63787 | 0.67728 | 0.9568
174.5 | 2476.1755 | 0.63617 | 0.67548 | 0.95425
174.6 | 2476.239 | 0.63447 | 0.67368 | 0.95171
174.7 | 2476.3023 | 0.63278 | 0.67189 | 0.94917
174.8 | 2476.3654 | 0.6311 | 0.6701 | 0.94665
174.9 | 2476.4283 | 0.62942 | 0.66831 | 0.94413
175 | 2476.4911 | 0.62774 | 0.66653 | 0.94161
175.1 | 2476.5537 | 0.62607 | 0.66476 | 0.9391
175.2 | 2476.6161 | 0.6244 | 0.66299 | 0.9366
175.3 | 2476.6784 | 0.62274 | 0.66122 | 0.93411
175.4 | 2476.7405 | 0.62108 | 0.65946 | 0.93162
175.5 | 2476.8025 | 0.61943 | 0.65771 | 0.92914
175.6 | 2476.8642 | 0.61778 | 0.65595 | 0.92667
175.7 | 2476.9259 | 0.61613 | 0.65421 | 0.9242
175.8 | 2476.9873 | 0.61449 | 0.65247 | 0.92174
175.9 | 2477.0486 | 0.61285 | 0.65073 | 0.91928
176 | 2477.1097 | 0.61122 | 0.64899 | 0.91683
176.1 | 2477.1707 | 0.60959 | 0.64727 | 0.91439
176.2 | 2477.2315 | 0.60797 | 0.64554 | 0.91196
176.3 | 2477.2921 | 0.60635 | 0.64382 | 0.90953
176.4 | 2477.3526 | 0.60474 | 0.64211 | 0.90711
176.5 | 2477.4129 | 0.60313 | 0.6404 | 0.90469
176.6 | 2477.473 | 0.60152 | 0.63869 | 0.90228
176.7 | 2477.533 | 0.59992 | 0.63699 | 0.89988
176.8 | 2477.5929 | 0.59832 | 0.6353 | 0.89748
176.9 | 2477.6525 | 0.59673 | 0.6336 | 0.89509
177 | 2477.7121 | 0.59514 | 0.63192 | 0.89271
177.1 | 2477.7714 | 0.59355 | 0.63023 | 0.89033
177.2 | 2477.8306 | 0.59197 | 0.62856 | 0.88796
177.3 | 2477.8896 | 0.5904 | 0.62688 | 0.88559
177.4 | 2477.9485 | 0.58882 | 0.62521 | 0.88324
177.5 | 2478.0073 | 0.58726 | 0.62355 | 0.88088
177.6 | 2478.0658 | 0.58569 | 0.62189 | 0.87854
177.7 | 2478.1242 | 0.58413 | 0.62023 | 0.8762
177.8 | 2478.1825 | 0.58258 | 0.61858 | 0.87386
177.9 | 2478.2406 | 0.58103 | 0.61693 | 0.87154
178 | 2478.2985 | 0.57948 | 0.61529 | 0.86922
178.1 | 2478.3563 | 0.57793 | 0.61365 | 0.8669
178.2 | 2478.414 | 0.5764 | 0.61202 | 0.86459
178.3 | 2478.4715 | 0.57486 | 0.61039 | 0.86229
178.4 | 2478.5288 | 0.57333 | 0.60876 | 0.85999
178.5 | 2478.586 | 0.5718 | 0.60714 | 0.8577
178.6 | 2478.643 | 0.57028 | 0.60552 | 0.85542
178.7 | 2478.6999 | 0.56876 | 0.60391 | 0.85314
178.8 | 2478.7566 | 0.56725 | 0.6023 | 0.85087
178.9 | 2478.8132 | 0.56574 | 0.6007 | 0.8486
179 | 2478.8696 | 0.56423 | 0.5991 | 0.84634
179.1 | 2478.9259 | 0.56273 | 0.5975 | 0.84409
179.2 | 2478.982 | 0.56123 | 0.59591 | 0.84184
179.3 | 2479.038 | 0.55973 | 0.59432 | 0.8396
179.4 | 2479.0938 | 0.55824 | 0.59274 | 0.83736
179.5 | 2479.1495 | 0.55676 | 0.59116 | 0.83513
179.6 | 2479.205 | 0.55527 | 0.58959 | 0.83291
179.7 | 2479.2604 | 0.55379 | 0.58802 | 0.83069
179.8 | 2479.3156 | 0.55232 | 0.58645 | 0.82848
179.9 | 2479.3707 | 0.55085 | 0.58489 | 0.82627
180 | 2479.4256 | 0.54938 | 0.58333 | 0.82407
180.1 | 2479.4804 | 0.54792 | 0.58178 | 0.82188
180.2 | 2479.5351 | 0.54646 | 0.58023 | 0.81969
180.3 | 2479.5896 | 0.545 | 0.57868 | 0.81751
180.4 | 2479.6439 | 0.54355 | 0.57714 | 0.81533
180.5 | 2479.6981 | 0.54211 | 0.57561 | 0.81316
180.6 | 2479.7522 | 0.54066 | 0.57407 | 0.81099
180.7 | 2479.8061 | 0.53922 | 0.57254 | 0.80883
180.8 | 2479.8599 | 0.53779 | 0.57102 | 0.80668
180.9 | 2479.9135 | 0.53635 | 0.5695 | 0.80453
181 | 2479.967 | 0.53493 | 0.56798 | 0.80239
181.1 | 2480.0204 | 0.5335 | 0.56647 | 0.80025
181.2 | 2480.0736 | 0.53208 | 0.56496 | 0.79812
181.3 | 2480.1267 | 0.53066 | 0.56346 | 0.79599
181.4 | 2480.1796 | 0.52925 | 0.56196 | 0.79387
181.5 | 2480.2324 | 0.52784 | 0.56046 | 0.79176
181.6 | 2480.285 | 0.52643 | 0.55897 | 0.78965
181.7 | 2480.3375 | 0.52503 | 0.55748 | 0.78755
181.8 | 2480.3899 | 0.52363 | 0.55599 | 0.78545
181.9 | 2480.4421 | 0.52224 | 0.55451 | 0.78336
182 | 2480.4942 | 0.52085 | 0.55304 | 0.78127
182.1 | 2480.5461 | 0.51946 | 0.55156 | 0.77919
182.2 | 2480.5979 | 0.51808 | 0.55009 | 0.77712
182.3 | 2480.6496 | 0.5167 | 0.54863 | 0.77505
182.4 | 2480.7011 | 0.51532 | 0.54717 | 0.77298
182.5 | 2480.7525 | 0.51395 | 0.54571 | 0.77093
182.6 | 2480.8038 | 0.51258 | 0.54426 | 0.76887
182.7 | 2480.8549 | 0.51122 | 0.54281 | 0.76683
182.8 | 2480.9059 | 0.50986 | 0.54136 | 0.76478
182.9 | 2480.9568 | 0.5085 | 0.53992 | 0.76275
183 | 2481.0075 | 0.50714 | 0.53848 | 0.76072
183.1 | 2481.058 | 0.50579 | 0.53705 | 0.75869
183.2 | 2481.1085 | 0.50445 | 0.53562 | 0.75667
183.3 | 2481.1588 | 0.5031 | 0.53419 | 0.75465
183.4 | 2481.209 | 0.50176 | 0.53277 | 0.75264
183.5 | 2481.259 | 0.50043 | 0.53135 | 0.75064
183.6 | 2481.3089 | 0.49909 | 0.52994 | 0.74864
183.7 | 2481.3587 | 0.49776 | 0.52853 | 0.74665
183.8 | 2481.4083 | 0.49644 | 0.52712 | 0.74466
183.9 | 2481.4579 | 0.49512 | 0.52571 | 0.74268
184 | 2481.5072 | 0.4938 | 0.52431 | 0.7407
184.1 | 2481.5565 | 0.49248 | 0.52292 | 0.73873
184.2 | 2481.6056 | 0.49117 | 0.52153 | 0.73676
184.3 | 2481.6546 | 0.48986 | 0.52014 | 0.7348
184.4 | 2481.7034 | 0.48856 | 0.51875 | 0.73284
184.5 | 2481.7522 | 0.48726 | 0.51737 | 0.73089
184.6 | 2481.8008 | 0.48596 | 0.51599 | 0.72894
184.7 | 2481.8492 | 0.48467 | 0.51462 | 0.727
184.8 | 2481.8976 | 0.48338 | 0.51325 | 0.72506
184.9 | 2481.9458 | 0.48209 | 0.51188 | 0.72313
185 | 2481.9939 | 0.4808 | 0.51052 | 0.72121
185.1 | 2482.0418 | 0.47952 | 0.50916 | 0.71929
185.2 | 2482.0896 | 0.47825 | 0.5078 | 0.71737
185.3 | 2482.1373 | 0.47697 | 0.50645 | 0.71546
185.4 | 2482.1849 | 0.4757 | 0.5051 | 0.71355
185.5 | 2482.2324 | 0.47444 | 0.50376 | 0.71165
185.6 | 2482.2797 | 0.47317 | 0.50241 | 0.70976
185.7 | 2482.3269 | 0.47191 | 0.50108 | 0.70787
185.8 | 2482.3739 | 0.47066 | 0.49974 | 0.70598
185.9 | 2482.4209 | 0.4694 | 0.49841 | 0.7041
186 | 2482.4677 | 0.46815 | 0.49708 | 0.70223
186.1 | 2482.5144 | 0.46691 | 0.49576 | 0.70036
186.2 | 2482.5609 | 0.46566 | 0.49444 | 0.69849
186.3 | 2482.6074 | 0.46442 | 0.49312 | 0.69663
186.4 | 2482.6537 | 0.46319 | 0.49181 | 0.69478
186.5 | 2482.6999 | 0.46195 | 0.4905 | 0.69293
186.6 | 2482.746 | 0.46072 | 0.48919 | 0.69108
186.7 | 2482.7919 | 0.45949 | 0.48789 | 0.68924
186.8 | 2482.8377 | 0.45827 | 0.48659 | 0.68741
186.9 | 2482.8834 | 0.45705 | 0.4853 | 0.68558
187 | 2482.929 | 0.45583 | 0.484 | 0.68375
187.1 | 2482.9745 | 0.45462 | 0.48271 | 0.68193
187.2 | 2483.0198 | 0.45341 | 0.48143 | 0.68011
187.3 | 2483.0651 | 0.4522 | 0.48015 | 0.6783
187.4 | 2483.1102 | 0.451 | 0.47887 | 0.6765
187.5 | 2483.1551 | 0.4498 | 0.47759 | 0.67469
187.6 | 2483.2 | 0.4486 | 0.47632 | 0.6729
187.7 | 2483.2447 | 0.4474 | 0.47505 | 0.67111
187.8 | 2483.2894 | 0.44621 | 0.47379 | 0.66932
187.9 | 2483.3339 | 0.44502 | 0.47253 | 0.66754
188 | 2483.3782 | 0.44384 | 0.47127 | 0.66576
188.1 | 2483.4225 | 0.44266 | 0.47001 | 0.66398
188.2 | 2483.4667 | 0.44148 | 0.46876 | 0.66222
188.3 | 2483.5107 | 0.4403 | 0.46751 | 0.66045
188.4 | 2483.5546 | 0.43913 | 0.46627 | 0.65869
188.5 | 2483.5984 | 0.43796 | 0.46502 | 0.65694
188.6 | 2483.6421 | 0.43679 | 0.46379 | 0.65519
188.7 | 2483.6856 | 0.43563 | 0.46255 | 0.65345
188.8 | 2483.7291 | 0.43447 | 0.46132 | 0.65171
188.9 | 2483.7724 | 0.43331 | 0.46009 | 0.64997
189 | 2483.8156 | 0.43216 | 0.45887 | 0.64824
189.1 | 2483.8587 | 0.43101 | 0.45764 | 0.64651
189.2 | 2483.9017 | 0.42986 | 0.45642 | 0.64479
189.3 | 2483.9446 | 0.42872 | 0.45521 | 0.64307
189.4 | 2483.9873 | 0.42757 | 0.454 | 0.64136
189.5 | 2484.03 | 0.42644 | 0.45279 | 0.63965
189.6 | 2484.0725 | 0.4253 | 0.45158 | 0.63795
189.7 | 2484.1149 | 0.42417 | 0.45038 | 0.63625
189.8 | 2484.1572 | 0.42304 | 0.44918 | 0.63456
189.9 | 2484.1994 | 0.42191 | 0.44798 | 0.63287
190 | 2484.2415 | 0.42079 | 0.44679 | 0.63118
190.1 | 2484.2835 | 0.41967 | 0.4456 | 0.6295
190.2 | 2484.3253 | 0.41855 | 0.44441 | 0.62782
190.3 | 2484.3671 | 0.41743 | 0.44323 | 0.62615
190.4 | 2484.4087 | 0.41632 | 0.44205 | 0.62448
190.5 | 2484.4502 | 0.41521 | 0.44087 | 0.62282
190.6 | 2484.4916 | 0.41411 | 0.4397 | 0.62116
190.7 | 2484.5329 | 0.41301 | 0.43853 | 0.61951
190.8 | 2484.5741 | 0.41191 | 0.43736 | 0.61786
190.9 | 2484.6152 | 0.41081 | 0.4362 | 0.61621
191 | 2484.6562 | 0.40971 | 0.43503 | 0.61457
191.1 | 2484.697 | 0.40862 | 0.43388 | 0.61294
191.2 | 2484.7378 | 0.40754 | 0.43272 | 0.6113
191.3 | 2484.7784 | 0.40645 | 0.43157 | 0.60967
191.4 | 2484.819 | 0.40537 | 0.43042 | 0.60805
191.5 | 2484.8594 | 0.40429 | 0.42927 | 0.60643
191.6 | 2484.8997 | 0.40321 | 0.42813 | 0.60482
191.7 | 2484.9399 | 0.40214 | 0.42699 | 0.60321
191.8 | 2484.98 | 0.40107 | 0.42585 | 0.6016
191.9 | 2485.02 | 0.4 | 0.42472 | 0.6
192 | 2485.0599 | 0.39893 | 0.42359 | 0.5984
192.1 | 2485.0997 | 0.39787 | 0.42246 | 0.59681
192.2 | 2485.1394 | 0.39681 | 0.42133 | 0.59522
192.3 | 2485.179 | 0.39575 | 0.42021 | 0.59363
192.4 | 2485.2185 | 0.3947 | 0.41909 | 0.59205
192.5 | 2485.2578 | 0.39365 | 0.41798 | 0.59047
192.6 | 2485.2971 | 0.3926 | 0.41686 | 0.5889
192.7 | 2485.3362 | 0.39156 | 0.41575 | 0.58733
192.8 | 2485.3753 | 0.39051 | 0.41465 | 0.58577
192.9 | 2485.4142 | 0.38947 | 0.41354 | 0.58421
193 | 2485.4531 | 0.38844 | 0.41244 | 0.58265
193.1 | 2485.4918 | 0.3874 | 0.41134 | 0.5811
193.2 | 2485.5305 | 0.38637 | 0.41025 | 0.57955
193.3 | 2485.569 | 0.38534 | 0.40915 | 0.57801
193.4 | 2485.6074 | 0.38431 | 0.40806 | 0.57647
193.5 | 2485.6458 | 0.38329 | 0.40698 | 0.57494
193.6 | 2485.684 | 0.38227 | 0.40589 | 0.57341
193.7 | 2485.7221 | 0.38125 | 0.40481 | 0.57188
193.8 | 2485.7601 | 0.38024 | 0.40373 | 0.57036
193.9 | 2485.798 | 0.37922 | 0.40266 | 0.56884
194 | 2485.8359 | 0.37821 | 0.40159 | 0.56732
194.1 | 2485.8736 | 0.37721 | 0.40052 | 0.56581
194.2 | 2485.9112 | 0.3762 | 0.39945 | 0.5643
194.3 | 2485.9487 | 0.3752 | 0.39839 | 0.5628
194.4 | 2485.9862 | 0.3742 | 0.39733 | 0.5613
194.5 | 2486.0235 | 0.3732 | 0.39627 | 0.55981
194.6 | 2486.0607 | 0.37221 | 0.39521 | 0.55832
194.7 | 2486.0978 | 0.37122 | 0.39416 | 0.55683
194.8 | 2486.1348 | 0.37023 | 0.39311 | 0.55535
194.9 | 2486.1718 | 0.36925 | 0.39206 | 0.55387
195 | 2486.2086 | 0.36826 | 0.39102 | 0.55239
195.1 | 2486.2453 | 0.36728 | 0.38998 | 0.55092
195.2 | 2486.2819 | 0.3663 | 0.38894 | 0.54945
195.3 | 2486.3185 | 0.36533 | 0.3879 | 0.54799
195.4 | 2486.3549 | 0.36435 | 0.38687 | 0.54653
195.5 | 2486.3913 | 0.36338 | 0.38584 | 0.54508
195.6 | 2486.4275 | 0.36242 | 0.38481 | 0.54362
195.7 | 2486.4636 | 0.36145 | 0.38379 | 0.54218
195.8 | 2486.4997 | 0.36049 | 0.38277 | 0.54073
195.9 | 2486.5356 | 0.35953 | 0.38175 | 0.53929
196 | 2486.5715 | 0.35857 | 0.38073 | 0.53786
196.1 | 2486.6073 | 0.35762 | 0.37972 | 0.53642
196.2 | 2486.6429 | 0.35666 | 0.37871 | 0.535
196.3 | 2486.6785 | 0.35571 | 0.3777 | 0.53357
196.4 | 2486.714 | 0.35477 | 0.37669 | 0.53215
196.5 | 2486.7494 | 0.35382 | 0.37569 | 0.53073
196.6 | 2486.7846 | 0.35288 | 0.37469 | 0.52932
196.7 | 2486.8198 | 0.35194 | 0.37369 | 0.52791
196.8 | 2486.8549 | 0.351 | 0.37269 | 0.5265
196.9 | 2486.8899 | 0.35007 | 0.3717 | 0.5251
197 | 2486.9249 | 0.34914 | 0.37071 | 0.5237
197.1 | 2486.9597 | 0.34821 | 0.36972 | 0.52231
197.2 | 2486.9944 | 0.34728 | 0.36874 | 0.52092
197.3 | 2487.029 | 0.34635 | 0.36776 | 0.51953
197.4 | 2487.0636 | 0.34543 | 0.36678 | 0.51815
197.5 | 2487.098 | 0.34451 | 0.3658 | 0.51677
197.6 | 2487.1324 | 0.34359 | 0.36483 | 0.51539
197.7 | 2487.1667 | 0.34268 | 0.36386 | 0.51402
197.8 | 2487.2008 | 0.34177 | 0.36289 | 0.51265
197.9 | 2487.2349 | 0.34086 | 0.36192 | 0.51128
198 | 2487.2689 | 0.33995 | 0.36096 | 0.50992
198.1 | 2487.3028 | 0.33904 | 0.36 | 0.50856
198.2 | 2487.3366 | 0.33814 | 0.35904 | 0.50721
198.3 | 2487.3704 | 0.33724 | 0.35808 | 0.50586
198.4 | 2487.404 | 0.33634 | 0.35713 | 0.50451
198.5 | 2487.4375 | 0.33545 | 0.35618 | 0.50317
198.6 | 2487.471 | 0.33455 | 0.35523 | 0.50183
198.7 | 2487.5044 | 0.33366 | 0.35428 | 0.50049
198.8 | 2487.5376 | 0.33277 | 0.35334 | 0.49916
198.9 | 2487.5708 | 0.33189 | 0.3524 | 0.49783
199 | 2487.6039 | 0.331 | 0.35146 | 0.4965
199.1 | 2487.6369 | 0.33012 | 0.35052 | 0.49518
199.2 | 2487.6699 | 0.32924 | 0.34959 | 0.49386
199.3 | 2487.7027 | 0.32837 | 0.34866 | 0.49255
199.4 | 2487.7355 | 0.32749 | 0.34773 | 0.49124
199.5 | 2487.7681 | 0.32662 | 0.3468 | 0.48993
199.6 | 2487.8007 | 0.32575 | 0.34588 | 0.48862
199.7 | 2487.8332 | 0.32488 | 0.34496 | 0.48732
199.8 | 2487.8656 | 0.32402 | 0.34404 | 0.48602
199.9 | 2487.8979 | 0.32315 | 0.34312 | 0.48473
200 | 2487.9301 | 0.32229 | 0.34221 | 0.48344
200.1 | 2487.9623 | 0.32143 | 0.3413 | 0.48215
200.2 | 2487.9943 | 0.32058 | 0.34039 | 0.48087
200.3 | 2488.0263 | 0.31972 | 0.33948 | 0.47959
200.4 | 2488.0582 | 0.31887 | 0.33858 | 0.47831
200.5 | 2488.09 | 0.31802 | 0.33768 | 0.47704
200.6 | 2488.1217 | 0.31718 | 0.33678 | 0.47577
200.7 | 2488.1533 | 0.31633 | 0.33588 | 0.4745
200.8 | 2488.1849 | 0.31549 | 0.33499 | 0.47324
200.9 | 2488.2164 | 0.31465 | 0.33409 | 0.47197
201 | 2488.2477 | 0.31381 | 0.3332 | 0.47072
201.1 | 2488.279 | 0.31298 | 0.33232 | 0.46946
201.2 | 2488.3102 | 0.31214 | 0.33143 | 0.46821
201.3 | 2488.3414 | 0.31131 | 0.33055 | 0.46697
201.4 | 2488.3724 | 0.31048 | 0.32967 | 0.46572
201.5 | 2488.4034 | 0.30966 | 0.32879 | 0.46448
201.6 | 2488.4343 | 0.30883 | 0.32792 | 0.46325
201.7 | 2488.4651 | 0.30801 | 0.32704 | 0.46201
201.8 | 2488.4958 | 0.30719 | 0.32617 | 0.46078
201.9 | 2488.5264 | 0.30637 | 0.3253 | 0.45956
202 | 2488.557 | 0.30555 | 0.32444 | 0.45833
202.1 | 2488.5875 | 0.30474 | 0.32357 | 0.45711
202.2 | 2488.6179 | 0.30393 | 0.32271 | 0.45589
202.3 | 2488.6482 | 0.30312 | 0.32185 | 0.45468
202.4 | 2488.6784 | 0.30231 | 0.32099 | 0.45347
202.5 | 2488.7085 | 0.30151 | 0.32014 | 0.45226
202.6 | 2488.7386 | 0.3007 | 0.31929 | 0.45106
202.7 | 2488.7686 | 0.2999 | 0.31844 | 0.44986
202.8 | 2488.7985 | 0.2991 | 0.31759 | 0.44866
202.9 | 2488.8283 | 0.29831 | 0.31674 | 0.44746
203 | 2488.8581 | 0.29751 | 0.3159 | 0.44627
203.1 | 2488.8878 | 0.29672 | 0.31506 | 0.44508
203.2 | 2488.9174 | 0.29593 | 0.31422 | 0.4439
203.3 | 2488.9469 | 0.29514 | 0.31338 | 0.44271
203.4 | 2488.9763 | 0.29436 | 0.31255 | 0.44154
203.5 | 2489.0057 | 0.29357 | 0.31172 | 0.44036
203.6 | 2489.035 | 0.29279 | 0.31089 | 0.43919
203.7 | 2489.0642 | 0.29201 | 0.31006 | 0.43802
203.8 | 2489.0933 | 0.29123 | 0.30923 | 0.43685
203.9 | 2489.1223 | 0.29046 | 0.30841 | 0.43569
204 | 2489.1513 | 0.28968 | 0.30759 | 0.43453
204.1 | 2489.1802 | 0.28891 | 0.30677 | 0.43337
204.2 | 2489.209 | 0.28814 | 0.30595 | 0.43222
204.3 | 2489.2377 | 0.28738 | 0.30514 | 0.43107
204.4 | 2489.2664 | 0.28661 | 0.30432 | 0.42992
204.5 | 2489.295 | 0.28585 | 0.30351 | 0.42877
204.6 | 2489.3235 | 0.28509 | 0.3027 | 0.42763
204.7 | 2489.3519 | 0.28433 | 0.3019 | 0.42649
204.8 | 2489.3803 | 0.28357 | 0.30109 | 0.42536
204.9 | 2489.4086 | 0.28282 | 0.30029 | 0.42422
205 | 2489.4368 | 0.28206 | 0.29949 | 0.42309
205.1 | 2489.4649 | 0.28131 | 0.2987 | 0.42197
205.2 | 2489.493 | 0.28056 | 0.2979 | 0.42084
205.3 | 2489.5209 | 0.27981 | 0.29711 | 0.41972
205.4 | 2489.5488 | 0.27907 | 0.29632 | 0.4186
205.5 | 2489.5767 | 0.27833 | 0.29553 | 0.41749
205.6 | 2489.6044 | 0.27759 | 0.29474 | 0.41638
205.7 | 2489.6321 | 0.27685 | 0.29395 | 0.41527
205.8 | 2489.6597 | 0.27611 | 0.29317 | 0.41416
205.9 | 2489.6873 | 0.27537 | 0.29239 | 0.41306
206 | 2489.7147 | 0.27464 | 0.29161 | 0.41196
206.1 | 2489.7421 | 0.27391 | 0.29084 | 0.41086
206.2 | 2489.7694 | 0.27318 | 0.29006 | 0.40977
206.3 | 2489.7967 | 0.27245 | 0.28929 | 0.40868
206.4 | 2489.8239 | 0.27173 | 0.28852 | 0.40759
206.5 | 2489.851 | 0.271 | 0.28775 | 0.4065
206.6 | 2489.878 | 0.27028 | 0.28698 | 0.40542
206.7 | 2489.9049 | 0.26956 | 0.28622 | 0.40434
206.8 | 2489.9318 | 0.26884 | 0.28546 | 0.40326
206.9 | 2489.9586 | 0.26813 | 0.2847 | 0.40219
207 | 2489.9854 | 0.26741 | 0.28394 | 0.40112
207.1 | 2490.0121 | 0.2667 | 0.28318 | 0.40005
207.2 | 2490.0386 | 0.26599 | 0.28243 | 0.39899
207.3 | 2490.0652 | 0.26528 | 0.28168 | 0.39792
207.4 | 2490.0916 | 0.26458 | 0.28093 | 0.39686
207.5 | 2490.118 | 0.26387 | 0.28018 | 0.39581
207.6 | 2490.1443 | 0.26317 | 0.27943 | 0.39475
207.7 | 2490.1706 | 0.26247 | 0.27869 | 0.3937
207.8 | 2490.1968 | 0.26177 | 0.27795 | 0.39265
207.9 | 2490.2229 | 0.26107 | 0.27721 | 0.39161
208 | 2490.2489 | 0.26038 | 0.27647 | 0.39056
208.1 | 2490.2749 | 0.25968 | 0.27573 | 0.38952
208.2 | 2490.3008 | 0.25899 | 0.275 | 0.38849
208.3 | 2490.3266 | 0.2583 | 0.27426 | 0.38745
208.4 | 2490.3524 | 0.25761 | 0.27353 | 0.38642
208.5 | 2490.3781 | 0.25693 | 0.27281 | 0.38539
208.6 | 2490.4037 | 0.25624 | 0.27208 | 0.38436
208.7 | 2490.4292 | 0.25556 | 0.27135 | 0.38334
208.8 | 2490.4547 | 0.25488 | 0.27063 | 0.38232
208.9 | 2490.4801 | 0.2542 | 0.26991 | 0.3813
209 | 2490.5055 | 0.25352 | 0.26919 | 0.38029
209.1 | 2490.5308 | 0.25285 | 0.26847 | 0.37927
209.2 | 2490.556 | 0.25218 | 0.26776 | 0.37826
209.3 | 2490.5812 | 0.2515 | 0.26705 | 0.37726
209.4 | 2490.6062 | 0.25083 | 0.26634 | 0.37625
209.5 | 2490.6313 | 0.25017 | 0.26563 | 0.37525
209.6 | 2490.6562 | 0.2495 | 0.26492 | 0.37425
209.7 | 2490.6811 | 0.24884 | 0.26421 | 0.37325
209.8 | 2490.7059 | 0.24817 | 0.26351 | 0.37226
209.9 | 2490.7307 | 0.24751 | 0.26281 | 0.37127
210 | 2490.7553 | 0.24685 | 0.26211 | 0.37028
210.1 | 2490.78 | 0.2462 | 0.26141 | 0.36929
210.2 | 2490.8045 | 0.24554 | 0.26071 | 0.36831
210.3 | 2490.829 | 0.24489 | 0.26002 | 0.36733
210.4 | 2490.8534 | 0.24423 | 0.25933 | 0.36635
210.5 | 2490.8778 | 0.24358 | 0.25864 | 0.36538
210.6 | 2490.9021 | 0.24294 | 0.25795 | 0.3644
210.7 | 2490.9263 | 0.24229 | 0.25726 | 0.36343
210.8 | 2490.9505 | 0.24164 | 0.25658 | 0.36246
210.9 | 2490.9746 | 0.241 | 0.25589 | 0.3615
211 | 2490.9986 | 0.24036 | 0.25521 | 0.36054
211.1 | 2491.0226 | 0.23972 | 0.25453 | 0.35958
211.2 | 2491.0465 | 0.23908 | 0.25385 | 0.35862
211.3 | 2491.0703 | 0.23844 | 0.25318 | 0.35766
211.4 | 2491.0941 | 0.23781 | 0.2525 | 0.35671
211.5 | 2491.1178 | 0.23717 | 0.25183 | 0.35576
211.6 | 2491.1415 | 0.23654 | 0.25116 | 0.35481
211.7 | 2491.1651 | 0.23591 | 0.25049 | 0.35387
211.8 | 2491.1886 | 0.23528 | 0.24982 | 0.35293
211.9 | 2491.2121 | 0.23466 | 0.24916 | 0.35199
212 | 2491.2355 | 0.23403 | 0.2485 | 0.35105
212.1 | 2491.2588 | 0.23341 | 0.24783 | 0.35011
212.2 | 2491.2821 | 0.23279 | 0.24717 | 0.34918
212.3 | 2491.3053 | 0.23217 | 0.24652 | 0.34825
212.4 | 2491.3285 | 0.23155 | 0.24586 | 0.34732
212.5 | 2491.3516 | 0.23093 | 0.2452 | 0.3464
212.6 | 2491.3746 | 0.23032 | 0.24455 | 0.34548
212.7 | 2491.3976 | 0.2297 | 0.2439 | 0.34456
212.8 | 2491.4205 | 0.22909 | 0.24325 | 0.34364
212.9 | 2491.4433 | 0.22848 | 0.2426 | 0.34272
213 | 2491.4661 | 0.22787 | 0.24196 | 0.34181
213.1 | 2491.4888 | 0.22727 | 0.24131 | 0.3409
213.2 | 2491.5115 | 0.22666 | 0.24067 | 0.33999
213.3 | 2491.5341 | 0.22606 | 0.24003 | 0.33909
213.4 | 2491.5566 | 0.22546 | 0.23939 | 0.33818
213.5 | 2491.5791 | 0.22486 | 0.23875 | 0.33728
213.6 | 2491.6016 | 0.22426 | 0.23812 | 0.33639
213.7 | 2491.6239 | 0.22366 | 0.23748 | 0.33549
213.8 | 2491.6462 | 0.22306 | 0.23685 | 0.3346
213.9 | 2491.6685 | 0.22247 | 0.23622 | 0.33371
214 | 2491.6907 | 0.22188 | 0.23559 | 0.33282
214.1 | 2491.7128 | 0.22129 | 0.23496 | 0.33193
214.2 | 2491.7349 | 0.2207 | 0.23434 | 0.33105
214.3 | 2491.7569 | 0.22011 | 0.23371 | 0.33016
214.4 | 2491.7788 | 0.21952 | 0.23309 | 0.32929
214.5 | 2491.8007 | 0.21894 | 0.23247 | 0.32841
214.6 | 2491.8226 | 0.21836 | 0.23185 | 0.32753
214.7 | 2491.8443 | 0.21777 | 0.23123 | 0.32666
214.8 | 2491.8661 | 0.21719 | 0.23062 | 0.32579
214.9 | 2491.8877 | 0.21662 | 0.23 | 0.32492
215 | 2491.9093 | 0.21604 | 0.22939 | 0.32406
215.1 | 2491.9309 | 0.21546 | 0.22878 | 0.3232
215.2 | 2491.9524 | 0.21489 | 0.22817 | 0.32234
215.3 | 2491.9738 | 0.21432 | 0.22756 | 0.32148
215.4 | 2491.9952 | 0.21375 | 0.22696 | 0.32062
215.5 | 2492.0165 | 0.21318 | 0.22635 | 0.31977
215.6 | 2492.0377 | 0.21261 | 0.22575 | 0.31892
215.7 | 2492.0589 | 0.21204 | 0.22515 | 0.31807
215.8 | 2492.0801 | 0.21148 | 0.22455 | 0.31722
215.9 | 2492.1012 | 0.21092 | 0.22395 | 0.31637
216 | 2492.1222 | 0.21035 | 0.22335 | 0.31553
216.1 | 2492.1432 | 0.20979 | 0.22276 | 0.31469
216.2 | 2492.1641 | 0.20924 | 0.22217 | 0.31385
216.3 | 2492.185 | 0.20868 | 0.22157 | 0.31302
216.4 | 2492.2058 | 0.20812 | 0.22098 | 0.31218
216.5 | 2492.2266 | 0.20757 | 0.2204 | 0.31135
216.6 | 2492.2473 | 0.20702 | 0.21981 | 0.31052
216.7 | 2492.2679 | 0.20646 | 0.21922 | 0.3097
216.8 | 2492.2885 | 0.20591 | 0.21864 | 0.30887
216.9 | 2492.309 | 0.20537 | 0.21806 | 0.30805
217 | 2492.3295 | 0.20482 | 0.21748 | 0.30723
217.1 | 2492.3499 | 0.20427 | 0.2169 | 0.30641
217.2 | 2492.3703 | 0.20373 | 0.21632 | 0.30559
217.3 | 2492.3906 | 0.20319 | 0.21574 | 0.30478
217.4 | 2492.4109 | 0.20265 | 0.21517 | 0.30397
217.5 | 2492.4311 | 0.20211 | 0.2146 | 0.30316
217.6 | 2492.4513 | 0.20157 | 0.21402 | 0.30235
217.7 | 2492.4714 | 0.20103 | 0.21345 | 0.30155
217.8 | 2492.4914 | 0.2005 | 0.21289 | 0.30074
217.9 | 2492.5114 | 0.19996 | 0.21232 | 0.29994
218 | 2492.5314 | 0.19943 | 0.21175 | 0.29914
218.1 | 2492.5513 | 0.1989 | 0.21119 | 0.29835
218.2 | 2492.5711 | 0.19837 | 0.21063 | 0.29755
218.3 | 2492.5909 | 0.19784 | 0.21007 | 0.29676
218.4 | 2492.6106 | 0.19731 | 0.20951 | 0.29597
218.5 | 2492.6303 | 0.19679 | 0.20895 | 0.29518
218.6 | 2492.6499 | 0.19626 | 0.20839 | 0.2944
218.7 | 2492.6695 | 0.19574 | 0.20784 | 0.29361
218.8 | 2492.689 | 0.19522 | 0.20728 | 0.29283
218.9 | 2492.7085 | 0.1947 | 0.20673 | 0.29205
219 | 2492.7279 | 0.19418 | 0.20618 | 0.29127
219.1 | 2492.7473 | 0.19366 | 0.20563 | 0.2905
219.2 | 2492.7666 | 0.19315 | 0.20508 | 0.28972
219.3 | 2492.7858 | 0.19263 | 0.20454 | 0.28895
219.4 | 2492.8051 | 0.19212 | 0.20399 | 0.28818
219.5 | 2492.8242 | 0.19161 | 0.20345 | 0.28741
219.6 | 2492.8433 | 0.1911 | 0.20291 | 0.28665
219.7 | 2492.8624 | 0.19059 | 0.20237 | 0.28589
219.8 | 2492.8814 | 0.19008 | 0.20183 | 0.28512
219.9 | 2492.9003 | 0.18958 | 0.20129 | 0.28437
220 | 2492.9193 | 0.18907 | 0.20076 | 0.28361
220.1 | 2492.9381 | 0.18857 | 0.20022 | 0.28285
220.2 | 2492.9569 | 0.18807 | 0.19969 | 0.2821
220.3 | 2492.9757 | 0.18757 | 0.19916 | 0.28135
220.4 | 2492.9944 | 0.18707 | 0.19863 | 0.2806
220.5 | 2493.013 | 0.18657 | 0.1981 | 0.27985
220.6 | 2493.0316 | 0.18607 | 0.19757 | 0.27911
220.7 | 2493.0502 | 0.18558 | 0.19704 | 0.27836
220.8 | 2493.0687 | 0.18508 | 0.19652 | 0.27762
220.9 | 2493.0872 | 0.18459 | 0.196 | 0.27688
221 | 2493.1056 | 0.1841 | 0.19547 | 0.27614
221.1 | 2493.1239 | 0.18361 | 0.19495 | 0.27541
221.2 | 2493.1423 | 0.18312 | 0.19443 | 0.27468
221.3 | 2493.1605 | 0.18263 | 0.19392 | 0.27394
221.4 | 2493.1787 | 0.18214 | 0.1934 | 0.27322
221.5 | 2493.1969 | 0.18166 | 0.19288 | 0.27249
221.6 | 2493.215 | 0.18117 | 0.19237 | 0.27176
221.7 | 2493.2331 | 0.18069 | 0.19186 | 0.27104
221.8 | 2493.2511 | 0.18021 | 0.19135 | 0.27032
221.9 | 2493.2691 | 0.17973 | 0.19084 | 0.2696
222 | 2493.287 | 0.17925 | 0.19033 | 0.26888
222.1 | 2493.3049 | 0.17877 | 0.18982 | 0.26816
222.2 | 2493.3227 | 0.1783 | 0.18932 | 0.26745
222.3 | 2493.3405 | 0.17782 | 0.18881 | 0.26674
222.4 | 2493.3582 | 0.17735 | 0.18831 | 0.26603
222.5 | 2493.3759 | 0.17688 | 0.18781 | 0.26532
222.6 | 2493.3936 | 0.17641 | 0.18731 | 0.26461
222.7 | 2493.4111 | 0.17594 | 0.18681 | 0.26391
222.8 | 2493.4287 | 0.17547 | 0.18631 | 0.2632
222.9 | 2493.4462 | 0.175 | 0.18582 | 0.2625
223 | 2493.4636 | 0.17454 | 0.18532 | 0.2618
223.1 | 2493.4811 | 0.17407 | 0.18483 | 0.26111
223.2 | 2493.4984 | 0.17361 | 0.18434 | 0.26041
223.3 | 2493.5157 | 0.17314 | 0.18384 | 0.25972
223.4 | 2493.533 | 0.17268 | 0.18336 | 0.25903
223.5 | 2493.5502 | 0.17222 | 0.18287 | 0.25834
223.6 | 2493.5674 | 0.17177 | 0.18238 | 0.25765
223.7 | 2493.5845 | 0.17131 | 0.18189 | 0.25696
223.8 | 2493.6016 | 0.17085 | 0.18141 | 0.25628
223.9 | 2493.6187 | 0.1704 | 0.18093 | 0.25559
224 | 2493.6356 | 0.16994 | 0.18044 | 0.25491
224.1 | 2493.6526 | 0.16949 | 0.17996 | 0.25424
224.2 | 2493.6695 | 0.16904 | 0.17948 | 0.25356
224.3 | 2493.6864 | 0.16859 | 0.17901 | 0.25288
224.4 | 2493.7032 | 0.16814 | 0.17853 | 0.25221
224.5 | 2493.7199 | 0.16769 | 0.17805 | 0.25154
224.6 | 2493.7367 | 0.16725 | 0.17758 | 0.25087
224.7 | 2493.7533 | 0.1668 | 0.17711 | 0.2502
224.8 | 2493.77 | 0.16636 | 0.17664 | 0.24953
224.9 | 2493.7866 | 0.16591 | 0.17617 | 0.24887
225 | 2493.8031 | 0.16547 | 0.1757 | 0.24821
225.1 | 2493.8196 | 0.16503 | 0.17523 | 0.24755
225.2 | 2493.8361 | 0.16459 | 0.17476 | 0.24689
225.3 | 2493.8525 | 0.16415 | 0.1743 | 0.24623
225.4 | 2493.8689 | 0.16372 | 0.17383 | 0.24557
225.5 | 2493.8852 | 0.16328 | 0.17337 | 0.24492
225.6 | 2493.9015 | 0.16284 | 0.17291 | 0.24427
225.7 | 2493.9177 | 0.16241 | 0.17245 | 0.24362
225.8 | 2493.9339 | 0.16198 | 0.17199 | 0.24297
225.9 | 2493.9501 | 0.16155 | 0.17153 | 0.24232
226 | 2493.9662 | 0.16112 | 0.17107 | 0.24167
226.1 | 2493.9823 | 0.16069 | 0.17062 | 0.24103
226.2 | 2493.9983 | 0.16026 | 0.17016 | 0.24039
226.3 | 2494.0143 | 0.15983 | 0.16971 | 0.23975
226.4 | 2494.0302 | 0.15941 | 0.16926 | 0.23911
226.5 | 2494.0461 | 0.15898 | 0.16881 | 0.23847
226.6 | 2494.062 | 0.15856 | 0.16836 | 0.23784
226.7 | 2494.0778 | 0.15814 | 0.16791 | 0.23721
226.8 | 2494.0935 | 0.15772 | 0.16746 | 0.23657
226.9 | 2494.1093 | 0.1573 | 0.16702 | 0.23594
227 | 2494.125 | 0.15688 | 0.16657 | 0.23532
227.1 | 2494.1406 | 0.15646 | 0.16613 | 0.23469
227.2 | 2494.1562 | 0.15604 | 0.16569 | 0.23406
227.3 | 2494.1718 | 0.15563 | 0.16524 | 0.23344
227.4 | 2494.1873 | 0.15521 | 0.1648 | 0.23282
227.5 | 2494.2028 | 0.1548 | 0.16437 | 0.2322
227.6 | 2494.2182 | 0.15439 | 0.16393 | 0.23158
227.7 | 2494.2336 | 0.15398 | 0.16349 | 0.23096
227.8 | 2494.249 | 0.15357 | 0.16306 | 0.23035
227.9 | 2494.2643 | 0.15316 | 0.16262 | 0.22973
228 | 2494.2796 | 0.15275 | 0.16219 | 0.22912
228.1 | 2494.2948 | 0.15234 | 0.16176 | 0.22851
228.2 | 2494.31 | 0.15194 | 0.16133 | 0.2279
228.3 | 2494.3251 | 0.15153 | 0.1609 | 0.2273
228.4 | 2494.3403 | 0.15113 | 0.16047 | 0.22669
228.5 | 2494.3553 | 0.15073 | 0.16004 | 0.22609
228.6 | 2494.3704 | 0.15032 | 0.15961 | 0.22549
228.7 | 2494.3853 | 0.14992 | 0.15919 | 0.22489
228.8 | 2494.4003 | 0.14952 | 0.15876 | 0.22429
228.9 | 2494.4152 | 0.14913 | 0.15834 | 0.22369
229 | 2494.4301 | 0.14873 | 0.15792 | 0.22309
229.1 | 2494.4449 | 0.14833 | 0.1575 | 0.2225
229.2 | 2494.4597 | 0.14794 | 0.15708 | 0.22191
229.3 | 2494.4745 | 0.14754 | 0.15666 | 0.22132
229.4 | 2494.4892 | 0.14715 | 0.15624 | 0.22073
229.5 | 2494.5039 | 0.14676 | 0.15583 | 0.22014
229.6 | 2494.5185 | 0.14637 | 0.15541 | 0.21955
229.7 | 2494.5331 | 0.14598 | 0.155 | 0.21897
229.8 | 2494.5477 | 0.14559 | 0.15459 | 0.21838
229.9 | 2494.5622 | 0.1452 | 0.15418 | 0.2178
230 | 2494.5767 | 0.14482 | 0.15376 | 0.21722
230.1 | 2494.5911 | 0.14443 | 0.15336 | 0.21664
230.2 | 2494.6055 | 0.14405 | 0.15295 | 0.21607
230.3 | 2494.6199 | 0.14366 | 0.15254 | 0.21549
230.4 | 2494.6342 | 0.14328 | 0.15213 | 0.21492
230.5 | 2494.6485 | 0.1429 | 0.15173 | 0.21435
230.6 | 2494.6627 | 0.14252 | 0.15132 | 0.21378
230.7 | 2494.677 | 0.14214 | 0.15092 | 0.21321
230.8 | 2494.6911 | 0.14176 | 0.15052 | 0.21264
230.9 | 2494.7053 | 0.14138 | 0.15012 | 0.21207
231 | 2494.7194 | 0.141 | 0.14972 | 0.21151
231.1 | 2494.7334 | 0.14063 | 0.14932 | 0.21094
231.2 | 2494.7475 | 0.14025 | 0.14892 | 0.21038
231.3 | 2494.7614 | 0.13988 | 0.14853 | 0.20982
231.4 | 2494.7754 | 0.13951 | 0.14813 | 0.20926
231.5 | 2494.7893 | 0.13914 | 0.14774 | 0.20871
231.6 | 2494.8032 | 0.13877 | 0.14734 | 0.20815
231.7 | 2494.817 | 0.1384 | 0.14695 | 0.2076
231.8 | 2494.8308 | 0.13803 | 0.14656 | 0.20704
231.9 | 2494.8446 | 0.13766 | 0.14617 | 0.20649
232 | 2494.8583 | 0.13729 | 0.14578 | 0.20594
232.1 | 2494.872 | 0.13693 | 0.14539 | 0.20539
232.2 | 2494.8857 | 0.13656 | 0.145 | 0.20485
232.3 | 2494.8993 | 0.1362 | 0.14462 | 0.2043
232.4 | 2494.9129 | 0.13584 | 0.14423 | 0.20376
232.5 | 2494.9264 | 0.13548 | 0.14385 | 0.20321
232.6 | 2494.9399 | 0.13512 | 0.14346 | 0.20267
232.7 | 2494.9534 | 0.13476 | 0.14308 | 0.20213
232.8 | 2494.9669 | 0.1344 | 0.1427 | 0.20159
232.9 | 2494.9803 | 0.13404 | 0.14232 | 0.20106
233 | 2494.9936 | 0.13368 | 0.14194 | 0.20052
233.1 | 2495.007 | 0.13333 | 0.14156 | 0.19999
233.2 | 2495.0203 | 0.13297 | 0.14119 | 0.19946
233.3 | 2495.0335 | 0.13262 | 0.14081 | 0.19892
233.4 | 2495.0467 | 0.13226 | 0.14044 | 0.19839
233.5 | 2495.0599 | 0.13191 | 0.14006 | 0.19787
233.6 | 2495.0731 | 0.13156 | 0.13969 | 0.19734
233.7 | 2495.0862 | 0.13121 | 0.13932 | 0.19681
233.8 | 2495.0993 | 0.13086 | 0.13895 | 0.19629
233.9 | 2495.1123 | 0.13051 | 0.13858 | 0.19577
234 | 2495.1254 | 0.13016 | 0.13821 | 0.19525
234.1 | 2495.1383 | 0.12982 | 0.13784 | 0.19473
234.2 | 2495.1513 | 0.12947 | 0.13747 | 0.19421
234.3 | 2495.1642 | 0.12913 | 0.13711 | 0.19369
234.4 | 2495.1771 | 0.12878 | 0.13674 | 0.19317
234.5 | 2495.1899 | 0.12844 | 0.13638 | 0.19266
234.6 | 2495.2027 | 0.1281 | 0.13601 | 0.19215
234.7 | 2495.2155 | 0.12776 | 0.13565 | 0.19163
234.8 | 2495.2283 | 0.12742 | 0.13529 | 0.19112
234.9 | 2495.241 | 0.12708 | 0.13493 | 0.19062
235 | 2495.2536 | 0.12674 | 0.13457 | 0.19011
235.1 | 2495.2663 | 0.1264 | 0.13421 | 0.1896
235.2 | 2495.2789 | 0.12606 | 0.13386 | 0.1891
235.3 | 2495.2915 | 0.12573 | 0.1335 | 0.18859
235.4 | 2495.304 | 0.12539 | 0.13314 | 0.18809
235.5 | 2495.3165 | 0.12506 | 0.13279 | 0.18759
235.6 | 2495.329 | 0.12473 | 0.13243 | 0.18709
235.7 | 2495.3414 | 0.12439 | 0.13208 | 0.18659
235.8 | 2495.3538 | 0.12406 | 0.13173 | 0.1861
235.9 | 2495.3662 | 0.12373 | 0.13138 | 0.1856
236 | 2495.3785 | 0.1234 | 0.13103 | 0.18511
236.1 | 2495.3908 | 0.12308 | 0.13068 | 0.18461
236.2 | 2495.4031 | 0.12275 | 0.13033 | 0.18412
236.3 | 2495.4154 | 0.12242 | 0.12999 | 0.18363
236.4 | 2495.4276 | 0.12209 | 0.12964 | 0.18314
236.5 | 2495.4397 | 0.12177 | 0.12929 | 0.18265
236.6 | 2495.4519 | 0.12144 | 0.12895 | 0.18217
236.7 | 2495.464 | 0.12112 | 0.12861 | 0.18168
236.8 | 2495.4761 | 0.1208 | 0.12826 | 0.1812
236.9 | 2495.4881 | 0.12048 | 0.12792 | 0.18072
237 | 2495.5001 | 0.12016 | 0.12758 | 0.18023
237.1 | 2495.5121 | 0.11984 | 0.12724 | 0.17975
237.2 | 2495.5241 | 0.11952 | 0.1269 | 0.17928
237.3 | 2495.536 | 0.1192 | 0.12657 | 0.1788
237.4 | 2495.5479 | 0.11888 | 0.12623 | 0.17832
237.5 | 2495.5597 | 0.11856 | 0.12589 | 0.17785
237.6 | 2495.5716 | 0.11825 | 0.12556 | 0.17737
237.7 | 2495.5834 | 0.11793 | 0.12522 | 0.1769
237.8 | 2495.5951 | 0.11762 | 0.12489 | 0.17643
237.9 | 2495.6069 | 0.11731 | 0.12456 | 0.17596
238 | 2495.6186 | 0.11699 | 0.12422 | 0.17549
238.1 | 2495.6302 | 0.11668 | 0.12389 | 0.17502
238.2 | 2495.6419 | 0.11637 | 0.12356 | 0.17456
238.3 | 2495.6535 | 0.11606 | 0.12323 | 0.17409
238.4 | 2495.665 | 0.11575 | 0.12291 | 0.17363
238.5 | 2495.6766 | 0.11544 | 0.12258 | 0.17317
238.6 | 2495.6881 | 0.11514 | 0.12225 | 0.17271
238.7 | 2495.6996 | 0.11483 | 0.12193 | 0.17225
238.8 | 2495.711 | 0.11453 | 0.1216 | 0.17179
238.9 | 2495.7225 | 0.11422 | 0.12128 | 0.17133
239 | 2495.7338 | 0.11392 | 0.12096 | 0.17087
239.1 | 2495.7452 | 0.11361 | 0.12063 | 0.17042
239.2 | 2495.7565 | 0.11331 | 0.12031 | 0.16996
239.3 | 2495.7678 | 0.11301 | 0.11999 | 0.16951
239.4 | 2495.7791 | 0.11271 | 0.11967 | 0.16906
239.5 | 2495.7904 | 0.11241 | 0.11935 | 0.16861
239.6 | 2495.8016 | 0.11211 | 0.11904 | 0.16816
239.7 | 2495.8127 | 0.11181 | 0.11872 | 0.16771
239.8 | 2495.8239 | 0.11151 | 0.1184 | 0.16727
239.9 | 2495.835 | 0.11121 | 0.11809 | 0.16682
240 | 2495.8461 | 0.11092 | 0.11777 | 0.16638
240.1 | 2495.8572 | 0.11062 | 0.11746 | 0.16593
240.2 | 2495.8682 | 0.11033 | 0.11715 | 0.16549
240.3 | 2495.8792 | 0.11003 | 0.11683 | 0.16505
240.4 | 2495.8902 | 0.10974 | 0.11652 | 0.16461
240.5 | 2495.9011 | 0.10945 | 0.11621 | 0.16417
240.6 | 2495.912 | 0.10916 | 0.1159 | 0.16374
240.7 | 2495.9229 | 0.10887 | 0.11559 | 0.1633
240.8 | 2495.9338 | 0.10858 | 0.11529 | 0.16287
240.9 | 2495.9446 | 0.10829 | 0.11498 | 0.16243
241 | 2495.9554 | 0.108 | 0.11467 | 0.162
241.1 | 2495.9662 | 0.10771 | 0.11437 | 0.16157
241.2 | 2495.9769 | 0.10743 | 0.11406 | 0.16114
241.3 | 2495.9876 | 0.10714 | 0.11376 | 0.16071
241.4 | 2495.9983 | 0.10685 | 0.11346 | 0.16028
241.5 | 2496.009 | 0.10657 | 0.11315 | 0.15985
241.6 | 2496.0196 | 0.10629 | 0.11285 | 0.15943
241.7 | 2496.0302 | 0.106 | 0.11255 | 0.159
241.8 | 2496.0408 | 0.10572 | 0.11225 | 0.15858
241.9 | 2496.0513 | 0.10544 | 0.11195 | 0.15816
242 | 2496.0618 | 0.10516 | 0.11166 | 0.15774
242.1 | 2496.0723 | 0.10488 | 0.11136 | 0.15732
242.2 | 2496.0828 | 0.1046 | 0.11106 | 0.1569
242.3 | 2496.0932 | 0.10432 | 0.11077 | 0.15648
242.4 | 2496.1036 | 0.10404 | 0.11047 | 0.15606
242.5 | 2496.114 | 0.10376 | 0.11018 | 0.15565
242.6 | 2496.1244 | 0.10349 | 0.10988 | 0.15523
242.7 | 2496.1347 | 0.10321 | 0.10959 | 0.15482
242.8 | 2496.145 | 0.10294 | 0.1093 | 0.15441
242.9 | 2496.1552 | 0.10266 | 0.10901 | 0.154
243 | 2496.1655 | 0.10239 | 0.10872 | 0.15359
243.1 | 2496.1757 | 0.10212 | 0.10843 | 0.15318
243.2 | 2496.1859 | 0.10185 | 0.10814 | 0.15277
243.3 | 2496.196 | 0.10157 | 0.10785 | 0.15236
243.4 | 2496.2062 | 0.1013 | 0.10756 | 0.15196
243.5 | 2496.2163 | 0.10103 | 0.10728 | 0.15155
243.6 | 2496.2263 | 0.10077 | 0.10699 | 0.15115
243.7 | 2496.2364 | 0.1005 | 0.10671 | 0.15075
243.8 | 2496.2464 | 0.10023 | 0.10642 | 0.15034
243.9 | 2496.2564 | 0.099962 | 0.10614 | 0.14994
244 | 2496.2664 | 0.099696 | 0.10586 | 0.14954
244.1 | 2496.2763 | 0.099431 | 0.10558 | 0.14915
244.2 | 2496.2862 | 0.099166 | 0.10529 | 0.14875
244.3 | 2496.2961 | 0.098902 | 0.10501 | 0.14835
244.4 | 2496.306 | 0.098638 | 0.10473 | 0.14796
244.5 | 2496.3158 | 0.098376 | 0.10446 | 0.14756
244.6 | 2496.3256 | 0.098114 | 0.10418 | 0.14717
244.7 | 2496.3354 | 0.097852 | 0.1039 | 0.14678
244.8 | 2496.3452 | 0.097592 | 0.10362 | 0.14639
244.9 | 2496.3549 | 0.097332 | 0.10335 | 0.146
245 | 2496.3646 | 0.097073 | 0.10307 | 0.14561
245.1 | 2496.3743 | 0.096814 | 0.1028 | 0.14522
245.2 | 2496.384 | 0.096556 | 0.10252 | 0.14483
245.3 | 2496.3936 | 0.096299 | 0.10225 | 0.14445
245.4 | 2496.4032 | 0.096043 | 0.10198 | 0.14406
245.5 | 2496.4128 | 0.095787 | 0.10171 | 0.14368
245.6 | 2496.4223 | 0.095532 | 0.10144 | 0.1433
245.7 | 2496.4319 | 0.095278 | 0.10117 | 0.14292
245.8 | 2496.4414 | 0.095024 | 0.1009 | 0.14254
245.9 | 2496.4508 | 0.094771 | 0.10063 | 0.14216
246 | 2496.4603 | 0.094518 | 0.10036 | 0.14178
246.1 | 2496.4697 | 0.094267 | 0.10009 | 0.1414
246.2 | 2496.4791 | 0.094016 | 0.099826 | 0.14102
246.3 | 2496.4885 | 0.093765 | 0.09956 | 0.14065
246.4 | 2496.4978 | 0.093516 | 0.099295 | 0.14027
246.5 | 2496.5072 | 0.093266 | 0.09903 | 0.1399
246.6 | 2496.5165 | 0.093018 | 0.098766 | 0.13953
246.7 | 2496.5257 | 0.09277 | 0.098503 | 0.13916
246.8 | 2496.535 | 0.092523 | 0.098241 | 0.13878
246.9 | 2496.5442 | 0.092277 | 0.097979 | 0.13842
247 | 2496.5534 | 0.092031 | 0.097719 | 0.13805
247.1 | 2496.5626 | 0.091786 | 0.097458 | 0.13768
247.2 | 2496.5718 | 0.091542 | 0.097199 | 0.13731
247.3 | 2496.5809 | 0.091298 | 0.09694 | 0.13695
247.4 | 2496.59 | 0.091055 | 0.096682 | 0.13658
247.5 | 2496.5991 | 0.090812 | 0.096424 | 0.13622
247.6 | 2496.6081 | 0.09057 | 0.096167 | 0.13586
247.7 | 2496.6172 | 0.090329 | 0.095911 | 0.13549
247.8 | 2496.6262 | 0.090089 | 0.095656 | 0.13513
247.9 | 2496.6352 | 0.089849 | 0.095401 | 0.13477
248 | 2496.6441 | 0.089609 | 0.095147 | 0.13441
248.1 | 2496.6531 | 0.089371 | 0.094894 | 0.13406
248.2 | 2496.662 | 0.089133 | 0.094641 | 0.1337
248.3 | 2496.6709 | 0.088895 | 0.094389 | 0.13334
248.4 | 2496.6797 | 0.088659 | 0.094138 | 0.13299
248.5 | 2496.6886 | 0.088423 | 0.093887 | 0.13263
248.6 | 2496.6974 | 0.088187 | 0.093637 | 0.13228
248.7 | 2496.7062 | 0.087952 | 0.093388 | 0.13193
248.8 | 2496.715 | 0.087718 | 0.093139 | 0.13158
248.9 | 2496.7237 | 0.087484 | 0.092891 | 0.13123
249 | 2496.7324 | 0.087251 | 0.092643 | 0.13088
249.1 | 2496.7411 | 0.087019 | 0.092397 | 0.13053
249.2 | 2496.7498 | 0.086787 | 0.092151 | 0.13018
249.3 | 2496.7585 | 0.086556 | 0.091905 | 0.12983
249.4 | 2496.7671 | 0.086326 | 0.09166 | 0.12949
249.5 | 2496.7757 | 0.086096 | 0.091416 | 0.12914
249.6 | 2496.7843 | 0.085867 | 0.091173 | 0.1288
249.7 | 2496.7929 | 0.085638 | 0.09093 | 0.12846
249.8 | 2496.8014 | 0.08541 | 0.090688 | 0.12811
249.9 | 2496.8099 | 0.085182 | 0.090446 | 0.12777
250 | 2496.8184 | 0.084955 | 0.090206 | 0.12743
250.1 | 2496.8269 | 0.084729 | 0.089965 | 0.12709
250.2 | 2496.8353 | 0.084504 | 0.089726 | 0.12676
250.3 | 2496.8438 | 0.084279 | 0.089487 | 0.12642
250.4 | 2496.8522 | 0.084054 | 0.089248 | 0.12608
250.5 | 2496.8606 | 0.08383 | 0.089011 | 0.12575
250.6 | 2496.8689 | 0.083607 | 0.088774 | 0.12541
250.7 | 2496.8773 | 0.083384 | 0.088537 | 0.12508
250.8 | 2496.8856 | 0.083162 | 0.088302 | 0.12474
250.9 | 2496.8939 | 0.082941 | 0.088066 | 0.12441
251 | 2496.9021 | 0.08272 | 0.087832 | 0.12408
251.1 | 2496.9104 | 0.0825 | 0.087598 | 0.12375
251.2 | 2496.9186 | 0.08228 | 0.087365 | 0.12342
251.3 | 2496.9268 | 0.082061 | 0.087132 | 0.12309
251.4 | 2496.935 | 0.081842 | 0.0869 | 0.12276
251.5 | 2496.9432 | 0.081624 | 0.086669 | 0.12244
251.6 | 2496.9513 | 0.081407 | 0.086438 | 0.12211
251.7 | 2496.9594 | 0.08119 | 0.086208 | 0.12179
251.8 | 2496.9675 | 0.080974 | 0.085978 | 0.12146
251.9 | 2496.9756 | 0.080758 | 0.085749 | 0.12114
252 | 2496.9837 | 0.080543 | 0.085521 | 0.12081
252.1 | 2496.9917 | 0.080329 | 0.085293 | 0.12049
252.2 | 2496.9997 | 0.080115 | 0.085066 | 0.12017
252.3 | 2497.0077 | 0.079901 | 0.084839 | 0.11985
252.4 | 2497.0157 | 0.079689 | 0.084613 | 0.11953
252.5 | 2497.0236 | 0.079476 | 0.084388 | 0.11921
252.6 | 2497.0315 | 0.079265 | 0.084163 | 0.1189
252.7 | 2497.0394 | 0.079054 | 0.083939 | 0.11858
252.8 | 2497.0473 | 0.078843 | 0.083716 | 0.11826
252.9 | 2497.0552 | 0.078633 | 0.083493 | 0.11795
253 | 2497.063 | 0.078424 | 0.08327 | 0.11764
253.1 | 2497.0708 | 0.078215 | 0.083048 | 0.11732
253.2 | 2497.0786 | 0.078007 | 0.082827 | 0.11701
253.3 | 2497.0864 | 0.077799 | 0.082607 | 0.1167
253.4 | 2497.0942 | 0.077592 | 0.082387 | 0.11639
253.5 | 2497.1019 | 0.077385 | 0.082167 | 0.11608
253.6 | 2497.1096 | 0.077179 | 0.081948 | 0.11577
253.7 | 2497.1173 | 0.076973 | 0.08173 | 0.11546
253.8 | 2497.125 | 0.076768 | 0.081513 | 0.11515
253.9 | 2497.1327 | 0.076564 | 0.081296 | 0.11485
254 | 2497.1403 | 0.07636 | 0.081079 | 0.11454
254.1 | 2497.1479 | 0.076157 | 0.080863 | 0.11424
254.2 | 2497.1555 | 0.075954 | 0.080648 | 0.11393
254.3 | 2497.1631 | 0.075752 | 0.080433 | 0.11363
254.4 | 2497.1707 | 0.07555 | 0.080219 | 0.11332
254.5 | 2497.1782 | 0.075349 | 0.080005 | 0.11302
254.6 | 2497.1857 | 0.075148 | 0.079792 | 0.11272
254.7 | 2497.1932 | 0.074948 | 0.07958 | 0.11242
254.8 | 2497.2007 | 0.074748 | 0.079368 | 0.11212
254.9 | 2497.2081 | 0.074549 | 0.079156 | 0.11182
255 | 2497.2156 | 0.074351 | 0.078945 | 0.11153
255.1 | 2497.223 | 0.074153 | 0.078735 | 0.11123
255.2 | 2497.2304 | 0.073955 | 0.078526 | 0.11093
255.3 | 2497.2377 | 0.073758 | 0.078316 | 0.11064
255.4 | 2497.2451 | 0.073562 | 0.078108 | 0.11034
255.5 | 2497.2524 | 0.073366 | 0.0779 | 0.11005
255.6 | 2497.2598 | 0.073171 | 0.077692 | 0.10976
255.7 | 2497.2671 | 0.072976 | 0.077486 | 0.10946
255.8 | 2497.2743 | 0.072781 | 0.077279 | 0.10917
255.9 | 2497.2816 | 0.072588 | 0.077073 | 0.10888
256 | 2497.2888 | 0.072394 | 0.076868 | 0.10859
256.1 | 2497.2961 | 0.072201 | 0.076663 | 0.1083
256.2 | 2497.3033 | 0.072009 | 0.076459 | 0.10801
256.3 | 2497.3104 | 0.071817 | 0.076256 | 0.10773
256.4 | 2497.3176 | 0.071626 | 0.076053 | 0.10744
256.5 | 2497.3247 | 0.071435 | 0.07585 | 0.10715
256.6 | 2497.3319 | 0.071245 | 0.075648 | 0.10687
256.7 | 2497.339 | 0.071055 | 0.075447 | 0.10658
256.8 | 2497.3461 | 0.070866 | 0.075246 | 0.1063
256.9 | 2497.3531 | 0.070678 | 0.075045 | 0.10602
257 | 2497.3602 | 0.070489 | 0.074845 | 0.10573
257.1 | 2497.3672 | 0.070302 | 0.074646 | 0.10545
257.2 | 2497.3742 | 0.070114 | 0.074447 | 0.10517
257.3 | 2497.3812 | 0.069928 | 0.074249 | 0.10489
257.4 | 2497.3882 | 0.069741 | 0.074051 | 0.10461
257.5 | 2497.3951 | 0.069556 | 0.073854 | 0.10433
257.6 | 2497.4021 | 0.06937 | 0.073657 | 0.10406
257.7 | 2497.409 | 0.069186 | 0.073461 | 0.10378
257.8 | 2497.4159 | 0.069001 | 0.073266 | 0.1035
257.9 | 2497.4228 | 0.068818 | 0.07307 | 0.10323
258 | 2497.4296 | 0.068634 | 0.072876 | 0.10295
258.1 | 2497.4365 | 0.068452 | 0.072682 | 0.10268
258.2 | 2497.4433 | 0.068269 | 0.072488 | 0.1024
258.3 | 2497.4501 | 0.068088 | 0.072295 | 0.10213
258.4 | 2497.4569 | 0.067906 | 0.072103 | 0.10186
258.5 | 2497.4637 | 0.067725 | 0.071911 | 0.10159
258.6 | 2497.4704 | 0.067545 | 0.071719 | 0.10132
258.7 | 2497.4772 | 0.067365 | 0.071528 | 0.10105
258.8 | 2497.4839 | 0.067186 | 0.071338 | 0.10078
258.9 | 2497.4906 | 0.067007 | 0.071148 | 0.10051
259 | 2497.4973 | 0.066828 | 0.070958 | 0.10024
259.1 | 2497.5039 | 0.06665 | 0.070769 | 0.099976
259.2 | 2497.5106 | 0.066473 | 0.070581 | 0.099709
259.3 | 2497.5172 | 0.066296 | 0.070393 | 0.099444
259.4 | 2497.5238 | 0.066119 | 0.070205 | 0.099179
259.5 | 2497.5304 | 0.065943 | 0.070018 | 0.098915
259.6 | 2497.537 | 0.065768 | 0.069832 | 0.098651
259.7 | 2497.5436 | 0.065592 | 0.069646 | 0.098389
259.8 | 2497.5501 | 0.065418 | 0.06946 | 0.098127
259.9 | 2497.5566 | 0.065244 | 0.069275 | 0.097865
260 | 2497.5631 | 0.06507 | 0.069091 | 0.097605
260.1 | 2497.5696 | 0.064897 | 0.068907 | 0.097345
260.2 | 2497.5761 | 0.064724 | 0.068723 | 0.097086
260.3 | 2497.5826 | 0.064551 | 0.06854 | 0.096827
260.4 | 2497.589 | 0.064379 | 0.068358 | 0.096569
260.5 | 2497.5954 | 0.064208 | 0.068176 | 0.096312
260.6 | 2497.6018 | 0.064037 | 0.067994 | 0.096055
260.7 | 2497.6082 | 0.063866 | 0.067813 | 0.0958
260.8 | 2497.6146 | 0.063696 | 0.067633 | 0.095545
260.9 | 2497.6209 | 0.063527 | 0.067453 | 0.09529
261 | 2497.6273 | 0.063358 | 0.067273 | 0.095036
261.1 | 2497.6336 | 0.063189 | 0.067094 | 0.094783
261.2 | 2497.6399 | 0.063021 | 0.066915 | 0.094531
261.3 | 2497.6462 | 0.062853 | 0.066737 | 0.094279
261.4 | 2497.6524 | 0.062685 | 0.066559 | 0.094028
261.5 | 2497.6587 | 0.062518 | 0.066382 | 0.093778
261.6 | 2497.6649 | 0.062352 | 0.066205 | 0.093528
261.7 | 2497.6711 | 0.062186 | 0.066029 | 0.093279
261.8 | 2497.6773 | 0.06202 | 0.065853 | 0.09303
261.9 | 2497.6835 | 0.061855 | 0.065678 | 0.092783
262 | 2497.6897 | 0.06169 | 0.065503 | 0.092536
262.1 | 2497.6958 | 0.061526 | 0.065328 | 0.092289
262.2 | 2497.702 | 0.061362 | 0.065154 | 0.092043
262.3 | 2497.7081 | 0.061199 | 0.064981 | 0.091798
262.4 | 2497.7142 | 0.061036 | 0.064808 | 0.091554
262.5 | 2497.7203 | 0.060873 | 0.064635 | 0.09131
262.6 | 2497.7264 | 0.060711 | 0.064463 | 0.091067
262.7 | 2497.7324 | 0.060549 | 0.064291 | 0.090824
262.8 | 2497.7385 | 0.060388 | 0.06412 | 0.090582
262.9 | 2497.7445 | 0.060227 | 0.063949 | 0.090341
263 | 2497.7505 | 0.060067 | 0.063779 | 0.090101
263.1 | 2497.7565 | 0.059907 | 0.063609 | 0.089861
263.2 | 2497.7625 | 0.059747 | 0.06344 | 0.089621
263.3 | 2497.7684 | 0.059588 | 0.063271 | 0.089383
263.4 | 2497.7744 | 0.05943 | 0.063102 | 0.089145
263.5 | 2497.7803 | 0.059271 | 0.062934 | 0.088907
263.6 | 2497.7862 | 0.059114 | 0.062767 | 0.08867
263.7 | 2497.7921 | 0.058956 | 0.0626 | 0.088434
263.8 | 2497.798 | 0.058799 | 0.062433 | 0.088199
263.9 | 2497.8038 | 0.058643 | 0.062267 | 0.087964
264 | 2497.8097 | 0.058486 | 0.062101 | 0.08773
264.1 | 2497.8155 | 0.058331 | 0.061935 | 0.087496
264.2 | 2497.8213 | 0.058175 | 0.06177 | 0.087263
264.3 | 2497.8271 | 0.05802 | 0.061606 | 0.087031
264.4 | 2497.8329 | 0.057866 | 0.061442 | 0.086799
264.5 | 2497.8387 | 0.057712 | 0.061278 | 0.086568
264.6 | 2497.8444 | 0.057558 | 0.061115 | 0.086337
264.7 | 2497.8502 | 0.057405 | 0.060952 | 0.086107
264.8 | 2497.8559 | 0.057252 | 0.06079 | 0.085878
264.9 | 2497.8616 | 0.057099 | 0.060628 | 0.085649
265 | 2497.8673 | 0.056947 | 0.060467 | 0.085421
265.1 | 2497.873 | 0.056796 | 0.060306 | 0.085194
265.2 | 2497.8787 | 0.056644 | 0.060145 | 0.084967
265.3 | 2497.8843 | 0.056494 | 0.059985 | 0.08474
265.4 | 2497.8899 | 0.056343 | 0.059825 | 0.084515
265.5 | 2497.8956 | 0.056193 | 0.059666 | 0.08429
265.6 | 2497.9012 | 0.056043 | 0.059507 | 0.084065
265.7 | 2497.9068 | 0.055894 | 0.059348 | 0.083841
265.8 | 2497.9123 | 0.055745 | 0.05919 | 0.083618
265.9 | 2497.9179 | 0.055597 | 0.059033 | 0.083395
266 | 2497.9234 | 0.055449 | 0.058875 | 0.083173
266.1 | 2497.929 | 0.055301 | 0.058719 | 0.082952
266.2 | 2497.9345 | 0.055154 | 0.058562 | 0.082731
266.3 | 2497.94 | 0.055007 | 0.058406 | 0.082511
266.4 | 2497.9455 | 0.054861 | 0.058251 | 0.082291
266.5 | 2497.9509 | 0.054714 | 0.058096 | 0.082072
266.6 | 2497.9564 | 0.054569 | 0.057941 | 0.081853
266.7 | 2497.9618 | 0.054423 | 0.057787 | 0.081635
266.8 | 2497.9673 | 0.054278 | 0.057633 | 0.081418
266.9 | 2497.9727 | 0.054134 | 0.057479 | 0.081201
267 | 2497.9781 | 0.05399 | 0.057326 | 0.080985
267.1 | 2497.9835 | 0.053846 | 0.057174 | 0.080769
267.2 | 2497.9888 | 0.053703 | 0.057021 | 0.080554
267.3 | 2497.9942 | 0.05356 | 0.056869 | 0.080339
267.4 | 2497.9995 | 0.053417 | 0.056718 | 0.080125
267.5 | 2498.0049 | 0.053275 | 0.056567 | 0.079912
267.6 | 2498.0102 | 0.053133 | 0.056416 | 0.079699
267.7 | 2498.0155 | 0.052991 | 0.056266 | 0.079487
267.8 | 2498.0208 | 0.05285 | 0.056116 | 0.079275
267.9 | 2498.026 | 0.052709 | 0.055967 | 0.079064
268 | 2498.0313 | 0.052569 | 0.055818 | 0.078854
268.1 | 2498.0365 | 0.052429 | 0.055669 | 0.078644
268.2 | 2498.0418 | 0.052289 | 0.055521 | 0.078434
268.3 | 2498.047 | 0.05215 | 0.055373 | 0.078225
268.4 | 2498.0522 | 0.052011 | 0.055225 | 0.078017
268.5 | 2498.0574 | 0.051873 | 0.055078 | 0.077809
268.6 | 2498.0625 | 0.051735 | 0.054932 | 0.077602
268.7 | 2498.0677 | 0.051597 | 0.054785 | 0.077395
268.8 | 2498.0728 | 0.051459 | 0.05464 | 0.077189
268.9 | 2498.078 | 0.051322 | 0.054494 | 0.076984
269 | 2498.0831 | 0.051186 | 0.054349 | 0.076779
269.1 | 2498.0882 | 0.051049 | 0.054204 | 0.076574
269.2 | 2498.0933 | 0.050913 | 0.05406 | 0.07637
269.3 | 2498.0984 | 0.050778 | 0.053916 | 0.076167
269.4 | 2498.1034 | 0.050643 | 0.053772 | 0.075964
269.5 | 2498.1085 | 0.050508 | 0.053629 | 0.075762
269.6 | 2498.1135 | 0.050373 | 0.053486 | 0.07556
269.7 | 2498.1185 | 0.050239 | 0.053344 | 0.075359
269.8 | 2498.1236 | 0.050105 | 0.053202 | 0.075158
269.9 | 2498.1286 | 0.049972 | 0.05306 | 0.074958
270 | 2498.1335 | 0.049839 | 0.052919 | 0.074758
270.1 | 2498.1385 | 0.049706 | 0.052778 | 0.074559
270.2 | 2498.1435 | 0.049574 | 0.052637 | 0.074361
270.3 | 2498.1484 | 0.049442 | 0.052497 | 0.074163
270.4 | 2498.1533 | 0.04931 | 0.052357 | 0.073965
270.5 | 2498.1583 | 0.049179 | 0.052218 | 0.073768
270.6 | 2498.1632 | 0.049048 | 0.052079 | 0.073572
270.7 | 2498.1681 | 0.048917 | 0.05194 | 0.073376
270.8 | 2498.1729 | 0.048787 | 0.051802 | 0.07318
270.9 | 2498.1778 | 0.048657 | 0.051664 | 0.072985
271 | 2498.1827 | 0.048527 | 0.051526 | 0.072791
271.1 | 2498.1875 | 0.048398 | 0.051389 | 0.072597
271.2 | 2498.1923 | 0.048269 | 0.051252 | 0.072404
271.3 | 2498.1971 | 0.048141 | 0.051116 | 0.072211
271.4 | 2498.2019 | 0.048012 | 0.05098 | 0.072019
271.5 | 2498.2067 | 0.047885 | 0.050844 | 0.071827
271.6 | 2498.2115 | 0.047757 | 0.050708 | 0.071636
271.7 | 2498.2163 | 0.04763 | 0.050573 | 0.071445
271.8 | 2498.221 | 0.047503 | 0.050439 | 0.071255
271.9 | 2498.2257 | 0.047377 | 0.050304 | 0.071065
272 | 2498.2305 | 0.04725 | 0.05017 | 0.070876
272.1 | 2498.2352 | 0.047125 | 0.050037 | 0.070687
272.2 | 2498.2399 | 0.046999 | 0.049903 | 0.070499
272.3 | 2498.2446 | 0.046874 | 0.049771 | 0.070311
272.4 | 2498.2492 | 0.046749 | 0.049638 | 0.070124
272.5 | 2498.2539 | 0.046625 | 0.049506 | 0.069937
272.6 | 2498.2586 | 0.0465 | 0.049374 | 0.069751
272.7 | 2498.2632 | 0.046377 | 0.049243 | 0.069565
272.8 | 2498.2678 | 0.046253 | 0.049111 | 0.06938
272.9 | 2498.2724 | 0.04613 | 0.048981 | 0.069195
273 | 2498.277 | 0.046007 | 0.04885 | 0.069011
273.1 | 2498.2816 | 0.045884 | 0.04872 | 0.068827
273.2 | 2498.2862 | 0.045762 | 0.04859 | 0.068643
273.3 | 2498.2908 | 0.04564 | 0.048461 | 0.068461
273.4 | 2498.2953 | 0.045519 | 0.048332 | 0.068278
273.5 | 2498.2999 | 0.045398 | 0.048203 | 0.068096
273.6 | 2498.3044 | 0.045277 | 0.048075 | 0.067915
273.7 | 2498.3089 | 0.045156 | 0.047947 | 0.067734
273.8 | 2498.3134 | 0.045036 | 0.047819 | 0.067554
273.9 | 2498.3179 | 0.044916 | 0.047692 | 0.067374
274 | 2498.3224 | 0.044796 | 0.047565 | 0.067195
274.1 | 2498.3268 | 0.044677 | 0.047438 | 0.067016
274.2 | 2498.3313 | 0.044558 | 0.047312 | 0.066837
274.3 | 2498.3357 | 0.044439 | 0.047186 | 0.066659
274.4 | 2498.3402 | 0.044321 | 0.04706 | 0.066482
274.5 | 2498.3446 | 0.044203 | 0.046935 | 0.066305
274.6 | 2498.349 | 0.044085 | 0.04681 | 0.066128
274.7 | 2498.3534 | 0.043968 | 0.046685 | 0.065952
274.8 | 2498.3578 | 0.043851 | 0.046561 | 0.065776
274.9 | 2498.3622 | 0.043734 | 0.046437 | 0.065601
275 | 2498.3665 | 0.043618 | 0.046313 | 0.065426
275.1 | 2498.3709 | 0.043501 | 0.04619 | 0.065252
275.2 | 2498.3752 | 0.043386 | 0.046067 | 0.065078
275.3 | 2498.3795 | 0.04327 | 0.045944 | 0.064905
275.4 | 2498.3839 | 0.043155 | 0.045822 | 0.064732
275.5 | 2498.3882 | 0.04304 | 0.0457 | 0.06456
275.6 | 2498.3924 | 0.042925 | 0.045578 | 0.064388
275.7 | 2498.3967 | 0.042811 | 0.045457 | 0.064216
275.8 | 2498.401 | 0.042697 | 0.045336 | 0.064045
275.9 | 2498.4053 | 0.042583 | 0.045215 | 0.063875
276 | 2498.4095 | 0.04247 | 0.045094 | 0.063705
276.1 | 2498.4137 | 0.042357 | 0.044974 | 0.063535
276.2 | 2498.418 | 0.042244 | 0.044855 | 0.063366
276.3 | 2498.4222 | 0.042131 | 0.044735 | 0.063197
276.4 | 2498.4264 | 0.042019 | 0.044616 | 0.063029
276.5 | 2498.4306 | 0.041907 | 0.044497 | 0.062861
276.6 | 2498.4347 | 0.041796 | 0.044379 | 0.062694
276.7 | 2498.4389 | 0.041684 | 0.04426 | 0.062527
276.8 | 2498.4431 | 0.041573 | 0.044143 | 0.06236
276.9 | 2498.4472 | 0.041463 | 0.044025 | 0.062194
277 | 2498.4514 | 0.041352 | 0.043908 | 0.062028
277.1 | 2498.4555 | 0.041242 | 0.043791 | 0.061863
277.2 | 2498.4596 | 0.041132 | 0.043674 | 0.061698
277.3 | 2498.4637 | 0.041023 | 0.043558 | 0.061534
277.4 | 2498.4678 | 0.040914 | 0.043442 | 0.06137
277.5 | 2498.4719 | 0.040805 | 0.043326 | 0.061207
277.6 | 2498.4759 | 0.040696 | 0.043211 | 0.061044
277.7 | 2498.48 | 0.040588 | 0.043096 | 0.060881
277.8 | 2498.484 | 0.040479 | 0.042981 | 0.060719
277.9 | 2498.4881 | 0.040372 | 0.042867 | 0.060557
278 | 2498.4921 | 0.040264 | 0.042752 | 0.060396
278.1 | 2498.4961 | 0.040157 | 0.042639 | 0.060235
278.2 | 2498.5001 | 0.04005 | 0.042525 | 0.060075
278.3 | 2498.5041 | 0.039943 | 0.042412 | 0.059915
278.4 | 2498.5081 | 0.039837 | 0.042299 | 0.059755
278.5 | 2498.5121 | 0.039731 | 0.042186 | 0.059596
278.6 | 2498.516 | 0.039625 | 0.042074 | 0.059438
278.7 | 2498.52 | 0.039519 | 0.041962 | 0.059279
278.8 | 2498.5239 | 0.039414 | 0.04185 | 0.059121
278.9 | 2498.5279 | 0.039309 | 0.041739 | 0.058964
279 | 2498.5318 | 0.039205 | 0.041627 | 0.058807
279.1 | 2498.5357 | 0.0391 | 0.041517 | 0.05865
279.2 | 2498.5396 | 0.038996 | 0.041406 | 0.058494
279.3 | 2498.5435 | 0.038892 | 0.041296 | 0.058338
279.4 | 2498.5474 | 0.038789 | 0.041186 | 0.058183
279.5 | 2498.5512 | 0.038685 | 0.041076 | 0.058028
279.6 | 2498.5551 | 0.038582 | 0.040967 | 0.057873
279.7 | 2498.5589 | 0.03848 | 0.040858 | 0.057719
279.8 | 2498.5628 | 0.038377 | 0.040749 | 0.057566
279.9 | 2498.5666 | 0.038275 | 0.04064 | 0.057412
280 | 2498.5704 | 0.038173 | 0.040532 | 0.057259
280.1 | 2498.5742 | 0.038071 | 0.040424 | 0.057107
280.2 | 2498.578 | 0.03797 | 0.040316 | 0.056955
280.3 | 2498.5818 | 0.037869 | 0.040209 | 0.056803
280.4 | 2498.5856 | 0.037768 | 0.040102 | 0.056652
280.5 | 2498.5894 | 0.037667 | 0.039995 | 0.056501
280.6 | 2498.5931 | 0.037567 | 0.039889 | 0.056351
280.7 | 2498.5969 | 0.037467 | 0.039782 | 0.056201
280.8 | 2498.6006 | 0.037367 | 0.039676 | 0.056051
280.9 | 2498.6043 | 0.037268 | 0.039571 | 0.055902
281 | 2498.608 | 0.037168 | 0.039465 | 0.055753
281.1 | 2498.6117 | 0.037069 | 0.03936 | 0.055604
281.2 | 2498.6154 | 0.036971 | 0.039255 | 0.055456
281.3 | 2498.6191 | 0.036872 | 0.039151 | 0.055308
281.4 | 2498.6228 | 0.036774 | 0.039047 | 0.055161
281.5 | 2498.6265 | 0.036676 | 0.038943 | 0.055014
281.6 | 2498.6301 | 0.036579 | 0.038839 | 0.054868
281.7 | 2498.6338 | 0.036481 | 0.038736 | 0.054722
281.8 | 2498.6374 | 0.036384 | 0.038632 | 0.054576
281.9 | 2498.641 | 0.036287 | 0.03853 | 0.054431
282 | 2498.6447 | 0.03619 | 0.038427 | 0.054286
282.1 | 2498.6483 | 0.036094 | 0.038325 | 0.054141
282.2 | 2498.6519 | 0.035998 | 0.038222 | 0.053997
282.3 | 2498.6555 | 0.035902 | 0.038121 | 0.053853
282.4 | 2498.659 | 0.035806 | 0.038019 | 0.05371
282.5 | 2498.6626 | 0.035711 | 0.037918 | 0.053567
282.6 | 2498.6662 | 0.035616 | 0.037817 | 0.053424
282.7 | 2498.6697 | 0.035521 | 0.037716 | 0.053282
282.8 | 2498.6733 | 0.035427 | 0.037616 | 0.05314
282.9 | 2498.6768 | 0.035332 | 0.037516 | 0.052998
283 | 2498.6803 | 0.035238 | 0.037416 | 0.052857
283.1 | 2498.6838 | 0.035144 | 0.037316 | 0.052716
283.2 | 2498.6874 | 0.035051 | 0.037217 | 0.052576
283.3 | 2498.6908 | 0.034957 | 0.037118 | 0.052436
283.4 | 2498.6943 | 0.034864 | 0.037019 | 0.052296
283.5 | 2498.6978 | 0.034771 | 0.03692 | 0.052157
283.6 | 2498.7013 | 0.034679 | 0.036822 | 0.052018
283.7 | 2498.7047 | 0.034586 | 0.036724 | 0.05188
283.8 | 2498.7082 | 0.034494 | 0.036626 | 0.051741
283.9 | 2498.7116 | 0.034402 | 0.036528 | 0.051604
284 | 2498.7151 | 0.034311 | 0.036431 | 0.051466
284.1 | 2498.7185 | 0.034219 | 0.036334 | 0.051329
284.2 | 2498.7219 | 0.034128 | 0.036237 | 0.051192
284.3 | 2498.7253 | 0.034037 | 0.036141 | 0.051056
284.4 | 2498.7287 | 0.033947 | 0.036045 | 0.05092
284.5 | 2498.7321 | 0.033856 | 0.035949 | 0.050785
284.6 | 2498.7355 | 0.033766 | 0.035853 | 0.050649
284.7 | 2498.7388 | 0.033676 | 0.035757 | 0.050514
284.8 | 2498.7422 | 0.033587 | 0.035662 | 0.05038
284.9 | 2498.7455 | 0.033497 | 0.035567 | 0.050246
285 | 2498.7489 | 0.033408 | 0.035472 | 0.050112
285.1 | 2498.7522 | 0.033319 | 0.035378 | 0.049978
285.2 | 2498.7555 | 0.03323 | 0.035284 | 0.049845
285.3 | 2498.7588 | 0.033142 | 0.03519 | 0.049713
285.4 | 2498.7621 | 0.033053 | 0.035096 | 0.04958
285.5 | 2498.7654 | 0.032965 | 0.035003 | 0.049448
285.6 | 2498.7687 | 0.032878 | 0.034909 | 0.049317
285.7 | 2498.772 | 0.03279 | 0.034816 | 0.049185
285.8 | 2498.7753 | 0.032703 | 0.034724 | 0.049054
285.9 | 2498.7785 | 0.032616 | 0.034631 | 0.048924
286 | 2498.7818 | 0.032529 | 0.034539 | 0.048793
286.1 | 2498.785 | 0.032442 | 0.034447 | 0.048663
286.2 | 2498.7883 | 0.032356 | 0.034355 | 0.048534
286.3 | 2498.7915 | 0.03227 | 0.034264 | 0.048404
286.4 | 2498.7947 | 0.032184 | 0.034173 | 0.048276
286.5 | 2498.7979 | 0.032098 | 0.034082 | 0.048147
286.6 | 2498.8011 | 0.032013 | 0.033991 | 0.048019
286.7 | 2498.8043 | 0.031927 | 0.0339 | 0.047891
286.8 | 2498.8075 | 0.031842 | 0.03381 | 0.047763
286.9 | 2498.8107 | 0.031757 | 0.03372 | 0.047636
287 | 2498.8139 | 0.031673 | 0.03363 | 0.047509
287.1 | 2498.817 | 0.031589 | 0.033541 | 0.047383
287.2 | 2498.8202 | 0.031504 | 0.033451 | 0.047257
287.3 | 2498.8233 | 0.031421 | 0.033362 | 0.047131
287.4 | 2498.8264 | 0.031337 | 0.033273 | 0.047005
287.5 | 2498.8296 | 0.031253 | 0.033185 | 0.04688
287.6 | 2498.8327 | 0.03117 | 0.033096 | 0.046755
287.7 | 2498.8358 | 0.031087 | 0.033008 | 0.046631
287.8 | 2498.8389 | 0.031004 | 0.03292 | 0.046507
287.9 | 2498.842 | 0.030922 | 0.032833 | 0.046383
288 | 2498.8451 | 0.030839 | 0.032745 | 0.046259
288.1 | 2498.8481 | 0.030757 | 0.032658 | 0.046136
288.2 | 2498.8512 | 0.030675 | 0.032571 | 0.046013
288.3 | 2498.8543 | 0.030594 | 0.032484 | 0.045891
288.4 | 2498.8573 | 0.030512 | 0.032398 | 0.045768
288.5 | 2498.8604 | 0.030431 | 0.032312 | 0.045646
288.6 | 2498.8634 | 0.03035 | 0.032225 | 0.045525
288.7 | 2498.8664 | 0.030269 | 0.03214 | 0.045404
288.8 | 2498.8694 | 0.030188 | 0.032054 | 0.045283
288.9 | 2498.8725 | 0.030108 | 0.031969 | 0.045162
289 | 2498.8755 | 0.030028 | 0.031884 | 0.045042
289.1 | 2498.8784 | 0.029948 | 0.031799 | 0.044922
289.2 | 2498.8814 | 0.029868 | 0.031714 | 0.044802
289.3 | 2498.8844 | 0.029789 | 0.03163 | 0.044683
289.4 | 2498.8874 | 0.029709 | 0.031545 | 0.044564
289.5 | 2498.8903 | 0.02963 | 0.031461 | 0.044445
289.6 | 2498.8933 | 0.029551 | 0.031377 | 0.044327
289.7 | 2498.8963 | 0.029473 | 0.031294 | 0.044209
289.8 | 2498.8992 | 0.029394 | 0.031211 | 0.044091
289.9 | 2498.9021 | 0.029316 | 0.031127 | 0.043974
290 | 2498.905 | 0.029238 | 0.031045 | 0.043857
290.1 | 2498.908 | 0.02916 | 0.030962 | 0.04374
290.2 | 2498.9109 | 0.029082 | 0.030879 | 0.043623
290.3 | 2498.9138 | 0.029005 | 0.030797 | 0.043507
290.4 | 2498.9167 | 0.028928 | 0.030715 | 0.043391
290.5 | 2498.9195 | 0.02885 | 0.030633 | 0.043276
290.6 | 2498.9224 | 0.028774 | 0.030552 | 0.043161
290.7 | 2498.9253 | 0.028697 | 0.03047 | 0.043046
290.8 | 2498.9282 | 0.028621 | 0.030389 | 0.042931
290.9 | 2498.931 | 0.028544 | 0.030308 | 0.042817
291 | 2498.9339 | 0.028468 | 0.030228 | 0.042703
291.1 | 2498.9367 | 0.028393 | 0.030147 | 0.042589
291.2 | 2498.9395 | 0.028317 | 0.030067 | 0.042475
291.3 | 2498.9424 | 0.028242 | 0.029987 | 0.042362
291.4 | 2498.9452 | 0.028166 | 0.029907 | 0.042249
291.5 | 2498.948 | 0.028091 | 0.029827 | 0.042137
291.6 | 2498.9508 | 0.028017 | 0.029748 | 0.042025
291.7 | 2498.9536 | 0.027942 | 0.029669 | 0.041913
291.8 | 2498.9564 | 0.027867 | 0.02959 | 0.041801
291.9 | 2498.9591 | 0.027793 | 0.029511 | 0.04169
292 | 2498.9619 | 0.027719 | 0.029432 | 0.041579
292.1 | 2498.9647 | 0.027645 | 0.029354 | 0.041468
292.2 | 2498.9674 | 0.027572 | 0.029276 | 0.041358
292.3 | 2498.9702 | 0.027498 | 0.029198 | 0.041248
292.4 | 2498.9729 | 0.027425 | 0.02912 | 0.041138
292.5 | 2498.9757 | 0.027352 | 0.029042 | 0.041028
292.6 | 2498.9784 | 0.027279 | 0.028965 | 0.040919
292.7 | 2498.9811 | 0.027207 | 0.028888 | 0.04081
292.8 | 2498.9838 | 0.027134 | 0.028811 | 0.040701
292.9 | 2498.9865 | 0.027062 | 0.028734 | 0.040593
293 | 2498.9892 | 0.02699 | 0.028658 | 0.040485
293.1 | 2498.9919 | 0.026918 | 0.028581 | 0.040377
293.2 | 2498.9946 | 0.026846 | 0.028505 | 0.040269
293.3 | 2498.9973 | 0.026775 | 0.028429 | 0.040162
293.4 | 2499 | 0.026703 | 0.028354 | 0.040055
293.5 | 2499.0026 | 0.026632 | 0.028278 | 0.039949
293.6 | 2499.0053 | 0.026561 | 0.028203 | 0.039842
293.7 | 2499.0079 | 0.026491 | 0.028128 | 0.039736
293.8 | 2499.0106 | 0.02642 | 0.028053 | 0.03963
293.9 | 2499.0132 | 0.02635 | 0.027978 | 0.039525
294 | 2499.0158 | 0.02628 | 0.027904 | 0.039419
294.1 | 2499.0184 | 0.02621 | 0.027829 | 0.039314
294.2 | 2499.0211 | 0.02614 | 0.027755 | 0.03921
294.3 | 2499.0237 | 0.02607 | 0.027681 | 0.039105
294.4 | 2499.0263 | 0.026001 | 0.027608 | 0.039001
294.5 | 2499.0289 | 0.025932 | 0.027534 | 0.038897
294.6 | 2499.0314 | 0.025862 | 0.027461 | 0.038794
294.7 | 2499.034 | 0.025794 | 0.027388 | 0.03869
294.8 | 2499.0366 | 0.025725 | 0.027315 | 0.038587
294.9 | 2499.0392 | 0.025656 | 0.027242 | 0.038485
295 | 2499.0417 | 0.025588 | 0.027169 | 0.038382
295.1 | 2499.0443 | 0.02552 | 0.027097 | 0.03828
295.2 | 2499.0468 | 0.025452 | 0.027025 | 0.038178
295.3 | 2499.0494 | 0.025384 | 0.026953 | 0.038076
295.4 | 2499.0519 | 0.025317 | 0.026881 | 0.037975
295.5 | 2499.0544 | 0.025249 | 0.02681 | 0.037874
295.6 | 2499.0569 | 0.025182 | 0.026738 | 0.037773
295.7 | 2499.0594 | 0.025115 | 0.026667 | 0.037672
295.8 | 2499.062 | 0.025048 | 0.026596 | 0.037572
295.9 | 2499.0644 | 0.024981 | 0.026525 | 0.037472
296 | 2499.0669 | 0.024915 | 0.026454 | 0.037372
296.1 | 2499.0694 | 0.024848 | 0.026384 | 0.037273
296.2 | 2499.0719 | 0.024782 | 0.026314 | 0.037173
296.3 | 2499.0744 | 0.024716 | 0.026244 | 0.037074
296.4 | 2499.0768 | 0.02465 | 0.026174 | 0.036976
296.5 | 2499.0793 | 0.024585 | 0.026104 | 0.036877
296.6 | 2499.0818 | 0.024519 | 0.026035 | 0.036779
296.7 | 2499.0842 | 0.024454 | 0.025965 | 0.036681
296.8 | 2499.0866 | 0.024389 | 0.025896 | 0.036583
296.9 | 2499.0891 | 0.024324 | 0.025827 | 0.036486
297 | 2499.0915 | 0.024259 | 0.025758 | 0.036389
297.1 | 2499.0939 | 0.024195 | 0.02569 | 0.036292
297.2 | 2499.0963 | 0.02413 | 0.025621 | 0.036195
297.3 | 2499.0987 | 0.024066 | 0.025553 | 0.036099
297.4 | 2499.1011 | 0.024002 | 0.025485 | 0.036003
297.5 | 2499.1035 | 0.023938 | 0.025417 | 0.035907
297.6 | 2499.1059 | 0.023874 | 0.025349 | 0.035811
297.7 | 2499.1083 | 0.023811 | 0.025282 | 0.035716
297.8 | 2499.1107 | 0.023747 | 0.025215 | 0.035621
297.9 | 2499.113 | 0.023684 | 0.025147 | 0.035526
298 | 2499.1154 | 0.023621 | 0.025081 | 0.035431
298.1 | 2499.1178 | 0.023558 | 0.025014 | 0.035337
298.2 | 2499.1201 | 0.023495 | 0.024947 | 0.035243
298.3 | 2499.1224 | 0.023433 | 0.024881 | 0.035149
298.4 | 2499.1248 | 0.02337 | 0.024814 | 0.035055
298.5 | 2499.1271 | 0.023308 | 0.024748 | 0.034962
298.6 | 2499.1294 | 0.023246 | 0.024682 | 0.034869
298.7 | 2499.1318 | 0.023184 | 0.024617 | 0.034776
298.8 | 2499.1341 | 0.023122 | 0.024551 | 0.034683
298.9 | 2499.1364 | 0.023061 | 0.024486 | 0.034591
299 | 2499.1387 | 0.022999 | 0.024421 | 0.034499
299.1 | 2499.141 | 0.022938 | 0.024355 | 0.034407
299.2 | 2499.1433 | 0.022877 | 0.024291 | 0.034315
299.3 | 2499.1455 | 0.022816 | 0.024226 | 0.034224
299.4 | 2499.1478 | 0.022755 | 0.024161 | 0.034133
299.5 | 2499.1501 | 0.022695 | 0.024097 | 0.034042
299.6 | 2499.1523 | 0.022634 | 0.024033 | 0.033951
299.7 | 2499.1546 | 0.022574 | 0.023969 | 0.033861
299.8 | 2499.1569 | 0.022514 | 0.023905 | 0.033771
299.9 | 2499.1591 | 0.022454 | 0.023841 | 0.033681
300 | 2499.1613 | 0.022394 | 0.023778 | 0.033591
300.1 | 2499.1636 | 0.022334 | 0.023715 | 0.033502
300.2 | 2499.1658 | 0.022275 | 0.023651 | 0.033412
300.3 | 2499.168 | 0.022216 | 0.023588 | 0.033323
300.4 | 2499.1702 | 0.022156 | 0.023526 | 0.033235
300.5 | 2499.1725 | 0.022097 | 0.023463 | 0.033146
300.6 | 2499.1747 | 0.022039 | 0.023401 | 0.033058
300.7 | 2499.1769 | 0.02198 | 0.023338 | 0.03297
300.8 | 2499.179 | 0.021921 | 0.023276 | 0.032882
300.9 | 2499.1812 | 0.021863 | 0.023214 | 0.032794
301 | 2499.1834 | 0.021805 | 0.023152 | 0.032707
301.1 | 2499.1856 | 0.021747 | 0.023091 | 0.03262
301.2 | 2499.1878 | 0.021689 | 0.023029 | 0.032533
301.3 | 2499.1899 | 0.021631 | 0.022968 | 0.032446
301.4 | 2499.1921 | 0.021573 | 0.022907 | 0.03236
301.5 | 2499.1942 | 0.021516 | 0.022846 | 0.032274
301.6 | 2499.1964 | 0.021459 | 0.022785 | 0.032188
301.7 | 2499.1985 | 0.021401 | 0.022724 | 0.032102
301.8 | 2499.2006 | 0.021344 | 0.022664 | 0.032017
301.9 | 2499.2028 | 0.021288 | 0.022603 | 0.031931
302 | 2499.2049 | 0.021231 | 0.022543 | 0.031846
302.1 | 2499.207 | 0.021174 | 0.022483 | 0.031762
302.2 | 2499.2091 | 0.021118 | 0.022423 | 0.031677
302.3 | 2499.2112 | 0.021062 | 0.022363 | 0.031593
302.4 | 2499.2133 | 0.021006 | 0.022304 | 0.031509
302.5 | 2499.2154 | 0.02095 | 0.022244 | 0.031425
302.6 | 2499.2175 | 0.020894 | 0.022185 | 0.031341
302.7 | 2499.2196 | 0.020838 | 0.022126 | 0.031257
302.8 | 2499.2217 | 0.020783 | 0.022067 | 0.031174
302.9 | 2499.2238 | 0.020727 | 0.022008 | 0.031091
303 | 2499.2258 | 0.020672 | 0.02195 | 0.031008
303.1 | 2499.2279 | 0.020617 | 0.021891 | 0.030926
303.2 | 2499.2299 | 0.020562 | 0.021833 | 0.030843
303.3 | 2499.232 | 0.020508 | 0.021775 | 0.030761
303.4 | 2499.234 | 0.020453 | 0.021717 | 0.030679
303.5 | 2499.2361 | 0.020398 | 0.021659 | 0.030598
303.6 | 2499.2381 | 0.020344 | 0.021601 | 0.030516
303.7 | 2499.2401 | 0.02029 | 0.021544 | 0.030435
303.8 | 2499.2422 | 0.020236 | 0.021486 | 0.030354
303.9 | 2499.2442 | 0.020182 | 0.021429 | 0.030273
304 | 2499.2462 | 0.020128 | 0.021372 | 0.030192
304.1 | 2499.2482 | 0.020075 | 0.021315 | 0.030112
304.2 | 2499.2502 | 0.020021 | 0.021259 | 0.030032
304.3 | 2499.2522 | 0.019968 | 0.021202 | 0.029952
304.4 | 2499.2542 | 0.019915 | 0.021145 | 0.029872
304.5 | 2499.2562 | 0.019862 | 0.021089 | 0.029793
304.6 | 2499.2582 | 0.019809 | 0.021033 | 0.029713
304.7 | 2499.2601 | 0.019756 | 0.020977 | 0.029634
304.8 | 2499.2621 | 0.019703 | 0.020921 | 0.029555
304.9 | 2499.2641 | 0.019651 | 0.020865 | 0.029476
305 | 2499.266 | 0.019599 | 0.02081 | 0.029398
305.1 | 2499.268 | 0.019546 | 0.020754 | 0.02932
305.2 | 2499.2699 | 0.019494 | 0.020699 | 0.029242
305.3 | 2499.2719 | 0.019442 | 0.020644 | 0.029164
305.4 | 2499.2738 | 0.019391 | 0.020589 | 0.029086
305.5 | 2499.2758 | 0.019339 | 0.020534 | 0.029009
305.6 | 2499.2777 | 0.019288 | 0.020479 | 0.028931
305.7 | 2499.2796 | 0.019236 | 0.020425 | 0.028854
305.8 | 2499.2815 | 0.019185 | 0.020371 | 0.028777
305.9 | 2499.2834 | 0.019134 | 0.020316 | 0.028701
306 | 2499.2853 | 0.019083 | 0.020262 | 0.028624
306.1 | 2499.2872 | 0.019032 | 0.020208 | 0.028548
306.2 | 2499.2891 | 0.018981 | 0.020154 | 0.028472
306.3 | 2499.291 | 0.018931 | 0.020101 | 0.028396
306.4 | 2499.2929 | 0.01888 | 0.020047 | 0.028321
306.5 | 2499.2948 | 0.01883 | 0.019994 | 0.028245
306.6 | 2499.2967 | 0.01878 | 0.019941 | 0.02817
306.7 | 2499.2986 | 0.01873 | 0.019887 | 0.028095
306.8 | 2499.3004 | 0.01868 | 0.019835 | 0.02802
306.9 | 2499.3023 | 0.01863 | 0.019782 | 0.027946
307 | 2499.3041 | 0.018581 | 0.019729 | 0.027871
307.1 | 2499.306 | 0.018531 | 0.019676 | 0.027797
307.2 | 2499.3079 | 0.018482 | 0.019624 | 0.027723
307.3 | 2499.3097 | 0.018433 | 0.019572 | 0.027649
307.4 | 2499.3115 | 0.018384 | 0.01952 | 0.027575
307.5 | 2499.3134 | 0.018335 | 0.019468 | 0.027502
307.6 | 2499.3152 | 0.018286 | 0.019416 | 0.027429
307.7 | 2499.317 | 0.018237 | 0.019364 | 0.027356
307.8 | 2499.3188 | 0.018189 | 0.019313 | 0.027283
307.9 | 2499.3207 | 0.01814 | 0.019261 | 0.02721
308 | 2499.3225 | 0.018092 | 0.01921 | 0.027138
308.1 | 2499.3243 | 0.018044 | 0.019159 | 0.027065
308.2 | 2499.3261 | 0.017996 | 0.019108 | 0.026993
308.3 | 2499.3279 | 0.017948 | 0.019057 | 0.026922
308.4 | 2499.3296 | 0.0179 | 0.019006 | 0.02685
308.5 | 2499.3314 | 0.017852 | 0.018955 | 0.026778
308.6 | 2499.3332 | 0.017805 | 0.018905 | 0.026707
308.7 | 2499.335 | 0.017757 | 0.018855 | 0.026636
308.8 | 2499.3368 | 0.01771 | 0.018804 | 0.026565
308.9 | 2499.3385 | 0.017663 | 0.018754 | 0.026494
309 | 2499.3403 | 0.017616 | 0.018704 | 0.026424
309.1 | 2499.342 | 0.017569 | 0.018655 | 0.026353
309.2 | 2499.3438 | 0.017522 | 0.018605 | 0.026283
309.3 | 2499.3455 | 0.017475 | 0.018555 | 0.026213
309.4 | 2499.3473 | 0.017429 | 0.018506 | 0.026143
309.5 | 2499.349 | 0.017382 | 0.018457 | 0.026074
309.6 | 2499.3508 | 0.017336 | 0.018407 | 0.026004
309.7 | 2499.3525 | 0.01729 | 0.018358 | 0.025935
309.8 | 2499.3542 | 0.017244 | 0.01831 | 0.025866
309.9 | 2499.3559 | 0.017198 | 0.018261 | 0.025797
310 | 2499.3576 | 0.017152 | 0.018212 | 0.025728
310.1 | 2499.3594 | 0.017107 | 0.018164 | 0.02566
310.2 | 2499.3611 | 0.017061 | 0.018115 | 0.025591
310.3 | 2499.3628 | 0.017016 | 0.018067 | 0.025523
310.4 | 2499.3645 | 0.01697 | 0.018019 | 0.025455
310.5 | 2499.3662 | 0.016925 | 0.017971 | 0.025388
310.6 | 2499.3678 | 0.01688 | 0.017923 | 0.02532
310.7 | 2499.3695 | 0.016835 | 0.017875 | 0.025253
310.8 | 2499.3712 | 0.01679 | 0.017828 | 0.025185
310.9 | 2499.3729 | 0.016745 | 0.01778 | 0.025118
311 | 2499.3746 | 0.016701 | 0.017733 | 0.025051
311.1 | 2499.3762 | 0.016656 | 0.017686 | 0.024985
311.2 | 2499.3779 | 0.016612 | 0.017639 | 0.024918
311.3 | 2499.3795 | 0.016568 | 0.017592 | 0.024852
311.4 | 2499.3812 | 0.016524 | 0.017545 | 0.024786
311.5 | 2499.3828 | 0.01648 | 0.017498 | 0.02472
311.6 | 2499.3845 | 0.016436 | 0.017451 | 0.024654
311.7 | 2499.3861 | 0.016392 | 0.017405 | 0.024588
311.8 | 2499.3878 | 0.016348 | 0.017359 | 0.024523
311.9 | 2499.3894 | 0.016305 | 0.017312 | 0.024457
312 | 2499.391 | 0.016261 | 0.017266 | 0.024392
312.1 | 2499.3926 | 0.016218 | 0.01722 | 0.024327
312.2 | 2499.3942 | 0.016175 | 0.017174 | 0.024262
312.3 | 2499.3959 | 0.016132 | 0.017129 | 0.024198
312.4 | 2499.3975 | 0.016089 | 0.017083 | 0.024133
312.5 | 2499.3991 | 0.016046 | 0.017038 | 0.024069
312.6 | 2499.4007 | 0.016003 | 0.016992 | 0.024005
312.7 | 2499.4023 | 0.015961 | 0.016947 | 0.023941
312.8 | 2499.4039 | 0.015918 | 0.016902 | 0.023877
312.9 | 2499.4055 | 0.015876 | 0.016857 | 0.023814
313 | 2499.407 | 0.015833 | 0.016812 | 0.02375
313.1 | 2499.4086 | 0.015791 | 0.016767 | 0.023687
313.2 | 2499.4102 | 0.015749 | 0.016723 | 0.023624
313.3 | 2499.4118 | 0.015707 | 0.016678 | 0.023561
313.4 | 2499.4133 | 0.015665 | 0.016634 | 0.023498
313.5 | 2499.4149 | 0.015624 | 0.016589 | 0.023436
313.6 | 2499.4164 | 0.015582 | 0.016545 | 0.023373
313.7 | 2499.418 | 0.015541 | 0.016501 | 0.023311
313.8 | 2499.4196 | 0.015499 | 0.016457 | 0.023249
313.9 | 2499.4211 | 0.015458 | 0.016413 | 0.023187
314 | 2499.4226 | 0.015417 | 0.01637 | 0.023125
314.1 | 2499.4242 | 0.015376 | 0.016326 | 0.023064
314.2 | 2499.4257 | 0.015335 | 0.016283 | 0.023002
314.3 | 2499.4272 | 0.015294 | 0.016239 | 0.022941
314.4 | 2499.4288 | 0.015253 | 0.016196 | 0.02288
314.5 | 2499.4303 | 0.015213 | 0.016153 | 0.022819
314.6 | 2499.4318 | 0.015172 | 0.01611 | 0.022758
314.7 | 2499.4333 | 0.015132 | 0.016067 | 0.022698
314.8 | 2499.4348 | 0.015091 | 0.016024 | 0.022637
314.9 | 2499.4363 | 0.015051 | 0.015981 | 0.022577
315 | 2499.4378 | 0.015011 | 0.015939 | 0.022517
315.1 | 2499.4393 | 0.014971 | 0.015896 | 0.022457
315.2 | 2499.4408 | 0.014931 | 0.015854 | 0.022397
315.3 | 2499.4423 | 0.014892 | 0.015812 | 0.022337
315.4 | 2499.4438 | 0.014852 | 0.01577 | 0.022278
315.5 | 2499.4453 | 0.014812 | 0.015728 | 0.022219
315.6 | 2499.4468 | 0.014773 | 0.015686 | 0.022159
315.7 | 2499.4482 | 0.014734 | 0.015644 | 0.0221
315.8 | 2499.4497 | 0.014694 | 0.015602 | 0.022041
315.9 | 2499.4512 | 0.014655 | 0.015561 | 0.021983
316 | 2499.4526 | 0.014616 | 0.015519 | 0.021924
316.1 | 2499.4541 | 0.014577 | 0.015478 | 0.021866
316.2 | 2499.4555 | 0.014538 | 0.015437 | 0.021808
316.3 | 2499.457 | 0.0145 | 0.015396 | 0.02175
316.4 | 2499.4584 | 0.014461 | 0.015355 | 0.021692
316.5 | 2499.4599 | 0.014423 | 0.015314 | 0.021634
316.6 | 2499.4613 | 0.014384 | 0.015273 | 0.021576
316.7 | 2499.4627 | 0.014346 | 0.015232 | 0.021519
316.8 | 2499.4642 | 0.014308 | 0.015192 | 0.021461
316.9 | 2499.4656 | 0.01427 | 0.015151 | 0.021404
317 | 2499.467 | 0.014232 | 0.015111 | 0.021347
317.1 | 2499.4684 | 0.014194 | 0.015071 | 0.02129
317.2 | 2499.4699 | 0.014156 | 0.015031 | 0.021234
317.3 | 2499.4713 | 0.014118 | 0.014991 | 0.021177
317.4 | 2499.4727 | 0.014081 | 0.014951 | 0.021121
317.5 | 2499.4741 | 0.014043 | 0.014911 | 0.021065
317.6 | 2499.4755 | 0.014006 | 0.014871 | 0.021008
317.7 | 2499.4769 | 0.013968 | 0.014832 | 0.020953
317.8 | 2499.4783 | 0.013931 | 0.014792 | 0.020897
317.9 | 2499.4797 | 0.013894 | 0.014753 | 0.020841
318 | 2499.4811 | 0.013857 | 0.014713 | 0.020786
318.1 | 2499.4824 | 0.01382 | 0.014674 | 0.02073
318.2 | 2499.4838 | 0.013783 | 0.014635 | 0.020675
318.3 | 2499.4852 | 0.013747 | 0.014596 | 0.02062
318.4 | 2499.4866 | 0.01371 | 0.014557 | 0.020565
318.5 | 2499.4879 | 0.013674 | 0.014519 | 0.02051
318.6 | 2499.4893 | 0.013637 | 0.01448 | 0.020456
318.7 | 2499.4907 | 0.013601 | 0.014441 | 0.020401
318.8 | 2499.492 | 0.013565 | 0.014403 | 0.020347
318.9 | 2499.4934 | 0.013528 | 0.014364 | 0.020293
319 | 2499.4947 | 0.013492 | 0.014326 | 0.020239
319.1 | 2499.4961 | 0.013456 | 0.014288 | 0.020185
319.2 | 2499.4974 | 0.013421 | 0.01425 | 0.020131
319.3 | 2499.4987 | 0.013385 | 0.014212 | 0.020077
319.4 | 2499.5001 | 0.013349 | 0.014174 | 0.020024
319.5 | 2499.5014 | 0.013314 | 0.014136 | 0.019971
319.6 | 2499.5027 | 0.013278 | 0.014099 | 0.019917
319.7 | 2499.5041 | 0.013243 | 0.014061 | 0.019864
319.8 | 2499.5054 | 0.013208 | 0.014024 | 0.019811
319.9 | 2499.5067 | 0.013172 | 0.013986 | 0.019759
320 | 2499.508 | 0.013137 | 0.013949 | 0.019706
320.1 | 2499.5093 | 0.013102 | 0.013912 | 0.019654
320.2 | 2499.5106 | 0.013067 | 0.013875 | 0.019601
320.3 | 2499.5119 | 0.013033 | 0.013838 | 0.019549
320.4 | 2499.5132 | 0.012998 | 0.013801 | 0.019497
320.5 | 2499.5145 | 0.012963 | 0.013764 | 0.019445
320.6 | 2499.5158 | 0.012929 | 0.013728 | 0.019393
320.7 | 2499.5171 | 0.012894 | 0.013691 | 0.019342
320.8 | 2499.5184 | 0.01286 | 0.013655 | 0.01929
320.9 | 2499.5197 | 0.012826 | 0.013618 | 0.019239
321 | 2499.521 | 0.012792 | 0.013582 | 0.019188
321.1 | 2499.5222 | 0.012758 | 0.013546 | 0.019136
321.2 | 2499.5235 | 0.012724 | 0.01351 | 0.019085
321.3 | 2499.5248 | 0.01269 | 0.013474 | 0.019035
321.4 | 2499.526 | 0.012656 | 0.013438 | 0.018984
321.5 | 2499.5273 | 0.012622 | 0.013402 | 0.018933
321.6 | 2499.5286 | 0.012589 | 0.013367 | 0.018883
321.7 | 2499.5298 | 0.012555 | 0.013331 | 0.018833
321.8 | 2499.5311 | 0.012522 | 0.013295 | 0.018783
321.9 | 2499.5323 | 0.012488 | 0.01326 | 0.018732
322 | 2499.5336 | 0.012455 | 0.013225 | 0.018683
322.1 | 2499.5348 | 0.012422 | 0.01319 | 0.018633
322.2 | 2499.536 | 0.012389 | 0.013154 | 0.018583
322.3 | 2499.5373 | 0.012356 | 0.013119 | 0.018534
322.4 | 2499.5385 | 0.012323 | 0.013084 | 0.018484
322.5 | 2499.5397 | 0.01229 | 0.01305 | 0.018435
322.6 | 2499.541 | 0.012257 | 0.013015 | 0.018386
322.7 | 2499.5422 | 0.012225 | 0.01298 | 0.018337
322.8 | 2499.5434 | 0.012192 | 0.012946 | 0.018288
322.9 | 2499.5446 | 0.01216 | 0.012911 | 0.01824
323 | 2499.5458 | 0.012127 | 0.012877 | 0.018191
323.1 | 2499.547 | 0.012095 | 0.012842 | 0.018143
323.2 | 2499.5482 | 0.012063 | 0.012808 | 0.018094
323.3 | 2499.5495 | 0.012031 | 0.012774 | 0.018046
323.4 | 2499.5507 | 0.011999 | 0.01274 | 0.017998
323.5 | 2499.5518 | 0.011967 | 0.012706 | 0.01795
323.6 | 2499.553 | 0.011935 | 0.012672 | 0.017902
323.7 | 2499.5542 | 0.011903 | 0.012639 | 0.017855
323.8 | 2499.5554 | 0.011871 | 0.012605 | 0.017807
323.9 | 2499.5566 | 0.01184 | 0.012571 | 0.01776
324 | 2499.5578 | 0.011808 | 0.012538 | 0.017712
324.1 | 2499.559 | 0.011777 | 0.012505 | 0.017665
324.2 | 2499.5601 | 0.011745 | 0.012471 | 0.017618
324.3 | 2499.5613 | 0.011714 | 0.012438 | 0.017571
324.4 | 2499.5625 | 0.011683 | 0.012405 | 0.017524
324.5 | 2499.5636 | 0.011652 | 0.012372 | 0.017478
324.6 | 2499.5648 | 0.011621 | 0.012339 | 0.017431
324.7 | 2499.566 | 0.01159 | 0.012306 | 0.017385
324.8 | 2499.5671 | 0.011559 | 0.012273 | 0.017338
324.9 | 2499.5683 | 0.011528 | 0.012241 | 0.017292
325 | 2499.5694 | 0.011497 | 0.012208 | 0.017246
325.1 | 2499.5706 | 0.011467 | 0.012175 | 0.0172
325.2 | 2499.5717 | 0.011436 | 0.012143 | 0.017154
325.3 | 2499.5729 | 0.011406 | 0.012111 | 0.017109
325.4 | 2499.574 | 0.011375 | 0.012078 | 0.017063
325.5 | 2499.5751 | 0.011345 | 0.012046 | 0.017018
325.6 | 2499.5763 | 0.011315 | 0.012014 | 0.016972
325.7 | 2499.5774 | 0.011285 | 0.011982 | 0.016927
325.8 | 2499.5785 | 0.011255 | 0.01195 | 0.016882
325.9 | 2499.5796 | 0.011225 | 0.011918 | 0.016837
326 | 2499.5807 | 0.011195 | 0.011887 | 0.016792
326.1 | 2499.5819 | 0.011165 | 0.011855 | 0.016748
326.2 | 2499.583 | 0.011135 | 0.011824 | 0.016703
326.3 | 2499.5841 | 0.011106 | 0.011792 | 0.016659
326.4 | 2499.5852 | 0.011076 | 0.011761 | 0.016614
326.5 | 2499.5863 | 0.011047 | 0.011729 | 0.01657
326.6 | 2499.5874 | 0.011017 | 0.011698 | 0.016526
326.7 | 2499.5885 | 0.010988 | 0.011667 | 0.016482
326.8 | 2499.5896 | 0.010959 | 0.011636 | 0.016438
326.9 | 2499.5907 | 0.010929 | 0.011605 | 0.016394
327 | 2499.5918 | 0.0109 | 0.011574 | 0.016351
327.1 | 2499.5929 | 0.010871 | 0.011543 | 0.016307
327.2 | 2499.594 | 0.010842 | 0.011512 | 0.016264
327.3 | 2499.595 | 0.010813 | 0.011482 | 0.01622
327.4 | 2499.5961 | 0.010785 | 0.011451 | 0.016177
327.5 | 2499.5972 | 0.010756 | 0.011421 | 0.016134
327.6 | 2499.5983 | 0.010727 | 0.01139 | 0.016091
327.7 | 2499.5993 | 0.010699 | 0.01136 | 0.016048
327.8 | 2499.6004 | 0.01067 | 0.01133 | 0.016005
327.9 | 2499.6015 | 0.010642 | 0.011299 | 0.015963
328 | 2499.6025 | 0.010614 | 0.011269 | 0.01592
328.1 | 2499.6036 | 0.010585 | 0.011239 | 0.015878
328.2 | 2499.6046 | 0.010557 | 0.011209 | 0.015836
328.3 | 2499.6057 | 0.010529 | 0.01118 | 0.015793
328.4 | 2499.6067 | 0.010501 | 0.01115 | 0.015751
328.5 | 2499.6078 | 0.010473 | 0.01112 | 0.015709
328.6 | 2499.6088 | 0.010445 | 0.011091 | 0.015668
328.7 | 2499.6099 | 0.010417 | 0.011061 | 0.015626
328.8 | 2499.6109 | 0.010389 | 0.011032 | 0.015584
328.9 | 2499.6119 | 0.010362 | 0.011002 | 0.015543
329 | 2499.613 | 0.010334 | 0.010973 | 0.015501
329.1 | 2499.614 | 0.010307 | 0.010944 | 0.01546
329.2 | 2499.615 | 0.010279 | 0.010914 | 0.015419
329.3 | 2499.6161 | 0.010252 | 0.010885 | 0.015378
329.4 | 2499.6171 | 0.010225 | 0.010856 | 0.015337
329.5 | 2499.6181 | 0.010197 | 0.010828 | 0.015296
329.6 | 2499.6191 | 0.01017 | 0.010799 | 0.015255
329.7 | 2499.6201 | 0.010143 | 0.01077 | 0.015215
329.8 | 2499.6212 | 0.010116 | 0.010741 | 0.015174
329.9 | 2499.6222 | 0.010089 | 0.010713 | 0.015134
330 | 2499.6232 | 0.010062 | 0.010684 | 0.015093
330.1 | 2499.6242 | 0.010035 | 0.010656 | 0.015053
330.2 | 2499.6252 | 0.010009 | 0.010627 | 0.015013
330.3 | 2499.6262 | 0.0099821 | 0.010599 | 0.014973
330.4 | 2499.6272 | 0.0099555 | 0.010571 | 0.014933
330.5 | 2499.6282 | 0.009929 | 0.010543 | 0.014894
330.6 | 2499.6291 | 0.0099026 | 0.010515 | 0.014854
330.7 | 2499.6301 | 0.0098762 | 0.010487 | 0.014814
330.8 | 2499.6311 | 0.0098499 | 0.010459 | 0.014775
330.9 | 2499.6321 | 0.0098237 | 0.010431 | 0.014735
331 | 2499.6331 | 0.0097975 | 0.010403 | 0.014696
331.1 | 2499.6341 | 0.0097714 | 0.010375 | 0.014657
331.2 | 2499.635 | 0.0097454 | 0.010348 | 0.014618
331.3 | 2499.636 | 0.0097194 | 0.01032 | 0.014579
331.4 | 2499.637 | 0.0096935 | 0.010293 | 0.01454
331.5 | 2499.6379 | 0.0096677 | 0.010265 | 0.014502
331.6 | 2499.6389 | 0.009642 | 0.010238 | 0.014463
331.7 | 2499.6399 | 0.0096163 | 0.010211 | 0.014424
331.8 | 2499.6408 | 0.0095907 | 0.010183 | 0.014386
331.9 | 2499.6418 | 0.0095652 | 0.010156 | 0.014348
332 | 2499.6427 | 0.0095397 | 0.010129 | 0.01431
332.1 | 2499.6437 | 0.0095143 | 0.010102 | 0.014271
332.2 | 2499.6446 | 0.0094889 | 0.010075 | 0.014233
332.3 | 2499.6456 | 0.0094637 | 0.010049 | 0.014196
332.4 | 2499.6465 | 0.0094385 | 0.010022 | 0.014158
332.5 | 2499.6475 | 0.0094133 | 0.0099951 | 0.01412
332.6 | 2499.6484 | 0.0093883 | 0.0099684 | 0.014082
332.7 | 2499.6493 | 0.0093633 | 0.0099419 | 0.014045
332.8 | 2499.6503 | 0.0093383 | 0.0099154 | 0.014007
332.9 | 2499.6512 | 0.0093135 | 0.009889 | 0.01397
333 | 2499.6521 | 0.0092887 | 0.0098627 | 0.013933
333.1 | 2499.6531 | 0.0092639 | 0.0098364 | 0.013896
333.2 | 2499.654 | 0.0092392 | 0.0098102 | 0.013859
333.3 | 2499.6549 | 0.0092146 | 0.0097841 | 0.013822
333.4 | 2499.6558 | 0.0091901 | 0.009758 | 0.013785
333.5 | 2499.6567 | 0.0091656 | 0.009732 | 0.013748
333.6 | 2499.6577 | 0.0091412 | 0.0097061 | 0.013712
333.7 | 2499.6586 | 0.0091169 | 0.0096803 | 0.013675
333.8 | 2499.6595 | 0.0090926 | 0.0096545 | 0.013639
333.9 | 2499.6604 | 0.0090684 | 0.0096288 | 0.013603
334 | 2499.6613 | 0.0090442 | 0.0096031 | 0.013566
334.1 | 2499.6622 | 0.0090201 | 0.0095776 | 0.01353
334.2 | 2499.6631 | 0.0089961 | 0.0095521 | 0.013494
334.3 | 2499.664 | 0.0089722 | 0.0095266 | 0.013458
334.4 | 2499.6649 | 0.0089483 | 0.0095013 | 0.013422
334.5 | 2499.6658 | 0.0089244 | 0.009476 | 0.013387
334.6 | 2499.6667 | 0.0089007 | 0.0094507 | 0.013351
334.7 | 2499.6676 | 0.008877 | 0.0094256 | 0.013315
334.8 | 2499.6684 | 0.0088533 | 0.0094005 | 0.01328
334.9 | 2499.6693 | 0.0088298 | 0.0093754 | 0.013245
335 | 2499.6702 | 0.0088062 | 0.0093504 | 0.013209
335.1 | 2499.6711 | 0.0087828 | 0.0093255 | 0.013174
335.2 | 2499.672 | 0.0087594 | 0.0093007 | 0.013139
335.3 | 2499.6728 | 0.0087361 | 0.0092759 | 0.013104
335.4 | 2499.6737 | 0.0087128 | 0.0092512 | 0.013069
335.5 | 2499.6746 | 0.0086896 | 0.0092266 | 0.013034
335.6 | 2499.6754 | 0.0086665 | 0.009202 | 0.013
335.7 | 2499.6763 | 0.0086434 | 0.0091775 | 0.012965
335.8 | 2499.6772 | 0.0086204 | 0.0091531 | 0.012931
335.9 | 2499.678 | 0.0085974 | 0.0091287 | 0.012896
336 | 2499.6789 | 0.0085745 | 0.0091044 | 0.012862
336.1 | 2499.6797 | 0.0085517 | 0.0090802 | 0.012828
336.2 | 2499.6806 | 0.0085289 | 0.009056 | 0.012793
336.3 | 2499.6814 | 0.0085062 | 0.0090319 | 0.012759
336.4 | 2499.6823 | 0.0084835 | 0.0090078 | 0.012725
336.5 | 2499.6831 | 0.0084609 | 0.0089838 | 0.012691
336.6 | 2499.684 | 0.0084384 | 0.0089599 | 0.012658
336.7 | 2499.6848 | 0.0084159 | 0.008936 | 0.012624
336.8 | 2499.6857 | 0.0083935 | 0.0089122 | 0.01259
336.9 | 2499.6865 | 0.0083712 | 0.0088885 | 0.012557
337 | 2499.6873 | 0.0083489 | 0.0088648 | 0.012523
337.1 | 2499.6882 | 0.0083266 | 0.0088412 | 0.01249
337.2 | 2499.689 | 0.0083045 | 0.0088177 | 0.012457
337.3 | 2499.6898 | 0.0082824 | 0.0087942 | 0.012424
337.4 | 2499.6907 | 0.0082603 | 0.0087708 | 0.01239
337.5 | 2499.6915 | 0.0082383 | 0.0087474 | 0.012357
337.6 | 2499.6923 | 0.0082164 | 0.0087241 | 0.012325
337.7 | 2499.6931 | 0.0081945 | 0.0087009 | 0.012292
337.8 | 2499.6939 | 0.0081727 | 0.0086777 | 0.012259
337.9 | 2499.6947 | 0.0081509 | 0.0086546 | 0.012226
338 | 2499.6956 | 0.0081292 | 0.0086316 | 0.012194
338.1 | 2499.6964 | 0.0081075 | 0.0086086 | 0.012161
338.2 | 2499.6972 | 0.0080859 | 0.0085856 | 0.012129
338.3 | 2499.698 | 0.0080644 | 0.0085628 | 0.012097
338.4 | 2499.6988 | 0.0080429 | 0.00854 | 0.012064
338.5 | 2499.6996 | 0.0080215 | 0.0085172 | 0.012032
338.6 | 2499.7004 | 0.0080002 | 0.0084945 | 0.012
338.7 | 2499.7012 | 0.0079788 | 0.0084719 | 0.011968
338.8 | 2499.702 | 0.0079576 | 0.0084494 | 0.011936
338.9 | 2499.7028 | 0.0079364 | 0.0084269 | 0.011905
339 | 2499.7036 | 0.0079153 | 0.0084044 | 0.011873
339.1 | 2499.7044 | 0.0078942 | 0.008382 | 0.011841
339.2 | 2499.7051 | 0.0078732 | 0.0083597 | 0.01181
339.3 | 2499.7059 | 0.0078522 | 0.0083375 | 0.011778
339.4 | 2499.7067 | 0.0078313 | 0.0083152 | 0.011747
339.5 | 2499.7075 | 0.0078104 | 0.0082931 | 0.011716
339.6 | 2499.7083 | 0.0077896 | 0.008271 | 0.011684
339.7 | 2499.7091 | 0.0077689 | 0.008249 | 0.011653
339.8 | 2499.7098 | 0.0077482 | 0.008227 | 0.011622
339.9 | 2499.7106 | 0.0077276 | 0.0082051 | 0.011591
340 | 2499.7114 | 0.007707 | 0.0081833 | 0.01156
340.1 | 2499.7121 | 0.0076865 | 0.0081615 | 0.01153
340.2 | 2499.7129 | 0.007666 | 0.0081397 | 0.011499
340.3 | 2499.7137 | 0.0076456 | 0.0081181 | 0.011468
340.4 | 2499.7144 | 0.0076252 | 0.0080964 | 0.011438
340.5 | 2499.7152 | 0.0076049 | 0.0080749 | 0.011407
340.6 | 2499.716 | 0.0075847 | 0.0080534 | 0.011377
340.7 | 2499.7167 | 0.0075645 | 0.0080319 | 0.011347
340.8 | 2499.7175 | 0.0075443 | 0.0080105 | 0.011316
340.9 | 2499.7182 | 0.0075242 | 0.0079892 | 0.011286
341 | 2499.719 | 0.0075042 | 0.0079679 | 0.011256
341.1 | 2499.7197 | 0.0074842 | 0.0079467 | 0.011226
341.2 | 2499.7205 | 0.0074643 | 0.0079255 | 0.011196
341.3 | 2499.7212 | 0.0074444 | 0.0079044 | 0.011167
341.4 | 2499.7219 | 0.0074246 | 0.0078834 | 0.011137
341.5 | 2499.7227 | 0.0074048 | 0.0078624 | 0.011107
341.6 | 2499.7234 | 0.0073851 | 0.0078415 | 0.011078
341.7 | 2499.7242 | 0.0073654 | 0.0078206 | 0.011048
341.8 | 2499.7249 | 0.0073458 | 0.0077997 | 0.011019
341.9 | 2499.7256 | 0.0073262 | 0.007779 | 0.010989
342 | 2499.7264 | 0.0073067 | 0.0077583 | 0.01096
342.1 | 2499.7271 | 0.0072873 | 0.0077376 | 0.010931
342.2 | 2499.7278 | 0.0072679 | 0.007717 | 0.010902
342.3 | 2499.7285 | 0.0072485 | 0.0076964 | 0.010873
342.4 | 2499.7293 | 0.0072292 | 0.0076759 | 0.010844
342.5 | 2499.73 | 0.0072099 | 0.0076555 | 0.010815
342.6 | 2499.7307 | 0.0071907 | 0.0076351 | 0.010786
342.7 | 2499.7314 | 0.0071716 | 0.0076148 | 0.010757
342.8 | 2499.7321 | 0.0071525 | 0.0075945 | 0.010729
342.9 | 2499.7329 | 0.0071334 | 0.0075743 | 0.0107
343 | 2499.7336 | 0.0071144 | 0.0075541 | 0.010672
343.1 | 2499.7343 | 0.0070955 | 0.007534 | 0.010643
343.2 | 2499.735 | 0.0070766 | 0.0075139 | 0.010615
343.3 | 2499.7357 | 0.0070578 | 0.0074939 | 0.010587
343.4 | 2499.7364 | 0.007039 | 0.007474 | 0.010558
343.5 | 2499.7371 | 0.0070202 | 0.0074541 | 0.01053
343.6 | 2499.7378 | 0.0070015 | 0.0074342 | 0.010502
343.7 | 2499.7385 | 0.0069829 | 0.0074144 | 0.010474
343.8 | 2499.7392 | 0.0069643 | 0.0073947 | 0.010446
343.9 | 2499.7399 | 0.0069457 | 0.007375 | 0.010419
344 | 2499.7406 | 0.0069272 | 0.0073553 | 0.010391
344.1 | 2499.7413 | 0.0069088 | 0.0073357 | 0.010363
344.2 | 2499.742 | 0.0068904 | 0.0073162 | 0.010336
344.3 | 2499.7426 | 0.006872 | 0.0072967 | 0.010308
344.4 | 2499.7433 | 0.0068537 | 0.0072773 | 0.010281
344.5 | 2499.744 | 0.0068355 | 0.0072579 | 0.010253
344.6 | 2499.7447 | 0.0068173 | 0.0072386 | 0.010226
344.7 | 2499.7454 | 0.0067991 | 0.0072193 | 0.010199
344.8 | 2499.7461 | 0.006781 | 0.0072001 | 0.010172
344.9 | 2499.7467 | 0.006763 | 0.0071809 | 0.010144
345 | 2499.7474 | 0.0067449 | 0.0071618 | 0.010117
345.1 | 2499.7481 | 0.006727 | 0.0071427 | 0.01009
345.2 | 2499.7487 | 0.0067091 | 0.0071237 | 0.010064
345.3 | 2499.7494 | 0.0066912 | 0.0071047 | 0.010037
345.4 | 2499.7501 | 0.0066734 | 0.0070858 | 0.01001
345.5 | 2499.7507 | 0.0066556 | 0.0070669 | 0.0099834
345.6 | 2499.7514 | 0.0066379 | 0.0070481 | 0.0099568
345.7 | 2499.7521 | 0.0066202 | 0.0070293 | 0.0099303
345.8 | 2499.7527 | 0.0066026 | 0.0070106 | 0.0099039
345.9 | 2499.7534 | 0.006585 | 0.0069919 | 0.0098775
346 | 2499.754 | 0.0065675 | 0.0069733 | 0.0098512
346.1 | 2499.7547 | 0.00655 | 0.0069547 | 0.009825
346.2 | 2499.7554 | 0.0065325 | 0.0069362 | 0.0097988
346.3 | 2499.756 | 0.0065151 | 0.0069178 | 0.0097727
346.4 | 2499.7567 | 0.0064978 | 0.0068993 | 0.0097467
346.5 | 2499.7573 | 0.0064805 | 0.006881 | 0.0097207
346.6 | 2499.758 | 0.0064632 | 0.0068626 | 0.0096948
346.7 | 2499.7586 | 0.006446 | 0.0068444 | 0.009669
346.8 | 2499.7592 | 0.0064288 | 0.0068261 | 0.0096433
346.9 | 2499.7599 | 0.0064117 | 0.0068079 | 0.0096176
347 | 2499.7605 | 0.0063946 | 0.0067898 | 0.009592
347.1 | 2499.7612 | 0.0063776 | 0.0067717 | 0.0095664
347.2 | 2499.7618 | 0.0063606 | 0.0067537 | 0.0095409
347.3 | 2499.7624 | 0.0063437 | 0.0067357 | 0.0095155
347.4 | 2499.7631 | 0.0063268 | 0.0067178 | 0.0094902
347.5 | 2499.7637 | 0.0063099 | 0.0066999 | 0.0094649
347.6 | 2499.7643 | 0.0062931 | 0.006682 | 0.0094397
347.7 | 2499.7649 | 0.0062764 | 0.0066643 | 0.0094146
347.8 | 2499.7656 | 0.0062597 | 0.0066465 | 0.0093895
347.9 | 2499.7662 | 0.006243 | 0.0066288 | 0.0093645
348 | 2499.7668 | 0.0062264 | 0.0066112 | 0.0093396
348.1 | 2499.7674 | 0.0062098 | 0.0065935 | 0.0093147
348.2 | 2499.7681 | 0.0061933 | 0.006576 | 0.0092899
348.3 | 2499.7687 | 0.0061768 | 0.0065585 | 0.0092651
348.4 | 2499.7693 | 0.0061603 | 0.006541 | 0.0092405
348.5 | 2499.7699 | 0.0061439 | 0.0065236 | 0.0092159
348.6 | 2499.7705 | 0.0061275 | 0.0065062 | 0.0091913
348.7 | 2499.7711 | 0.0061112 | 0.0064889 | 0.0091668
348.8 | 2499.7717 | 0.006095 | 0.0064716 | 0.0091424
348.9 | 2499.7724 | 0.0060787 | 0.0064544 | 0.0091181
349 | 2499.773 | 0.0060625 | 0.0064372 | 0.0090938
349.1 | 2499.7736 | 0.0060464 | 0.00642 | 0.0090696
349.2 | 2499.7742 | 0.0060303 | 0.0064029 | 0.0090454
349.3 | 2499.7748 | 0.0060142 | 0.0063859 | 0.0090213
349.4 | 2499.7754 | 0.0059982 | 0.0063689 | 0.0089973
349.5 | 2499.776 | 0.0059822 | 0.0063519 | 0.0089734
349.6 | 2499.7766 | 0.0059663 | 0.006335 | 0.0089495
349.7 | 2499.7772 | 0.0059504 | 0.0063181 | 0.0089256
349.8 | 2499.7778 | 0.0059346 | 0.0063013 | 0.0089018
349.9 | 2499.7783 | 0.0059188 | 0.0062845 | 0.0088781
350 | 2499.7789 | 0.005903 | 0.0062678 | 0.0088545